- GENERAL

  - SUMMARY

    - This Section specifies administrative and procedural requirements for Contract closeout including, but not limited to:

      - Project Record Set

      - Operation and Maintenance Manuals

      - Warranties and Bonds Manual

      - Demonstration  and Training

      - Cleaning

      - Owner’s Final Inspection

      - Substantial Completion

      - Final Completion, and

      - Final Acceptance

    - Related Sections

      - Section 01 33 00 – Submittal Procedures

      - Section 01 33 00.11 – Submittal Standards Requirements and Compliance Review Exhibit

      - Section 01 78 23 – Operation and Maintenance Data

      - Section 01 78 23.11 – Facilities Management Data Requirements for Operations and Maintenance

      - Section 01 78 36 – Warranties

      - Section 01 79 00 – Demonstration and Training

      - Section 01 91 00 – General Commissioning Requirements

      - Section 01 91 19 – Building Exterior Enclosure Commissioning

    - For additional specific construction Work, closeout requirements are described in Divisions 02 thru 49 of the Specifications.

  - PROJECT RECORD SET

    - General:  Project Record Set documents are the final design drawings and specifications that have been updated by the A/E to include all of the RFI, ASI, and other changes to the contract documents as well as the changes indicated on the Contractor’s final red-line as-built Drawings. Project Record documents must be maintained in electronic document form such as Microsoft Work, Excel, PDF, AutoCad, etc.

    - The Contractor shall be required to provide their final red-line as-built Drawings and Specifications as soon as possible and submit them to the Owner so that A/E can produce the final record set.

    - Contractor’s As-built Drawings:  Maintain red line prints of the bid set Contract Drawings and approved Shop Drawings.  Mark the drawings to show new information that was not shown on the bid set Drawings, and on the approved Shop Drawings, including the actual installation where the installation varies substantively from the work as originally shown.  Mark drawings to show conditions fully and accurately.  Where Shop Drawings are used, record a cross-reference at the corresponding location on the Drawings.  Give particular attention to concealed elements that would be difficult to measure and record at a later date.

      - Organize as-built Drawings in manageable sets, bind with durable paper cover sheets, and print suitable titles, dates, and other identification on the cover of each set.

      - Mark with reproducible pencil and distinguish between variations in separate categories of the Work.  Text size is to be 1/8” minimum.  Good basic drafting practice must be applied.

      - Show bid addenda items, Change Orders, and Request for Information (RFI) responses by their number and date the revisions with a “cloud” around the revision.

      - Keep accurate measurements of below-grade site work, including permanent shoring, in accordance with Section 01 71 23 “Field Engineering.”

      - Show mechanical dampers, valves, reheat boxes, cleanouts, and other equipment and items that require maintenance.

      - Show location of construction-concealed mechanical, electrical and plumbing (MEP) riser installations including, but not limited to, piping, ductwork, and conduits referenced to visible and accessible features.

      - Show field changes of dimensions and details.

      - X-out conditions not constructed and appropriately annotate "not constructed" to convey the actual as constructed condition.

    - As-built Specifications:  Maintain one (1) copy of the bid set Contract Specifications showing all addenda, substitutions, Change Orders, and RFIs.  Give particular attention to the selection of options, changes in product data, and information on elements engineered by the Contractor and note related as-built Drawing information, as appropriate.  Clear, legible documentation must be applied.

    - As-built Shop Drawings:  The Contractor shall comply with the following CAD (Computer-Aided Drafting) standards and requirements when preparing BIM and as-built Shop Drawings required by the Contract Documents.

      - Cover sheets shall contain a complete index of all sheets.

      - Symbols shown must be symbols used in the Contract Documents.

      - Standard drafting practice shall be:

        - Title block

          - All sheets shall have a title block.

          - Title block information is to be on the right side of the sheet.

          - Title blocks shall include the following information:

            - Date

            - University Project Name

            - University Project Number

            - University Facility Number (FACNUM)

            - Sheet name

            - Sheet number

            - Contractor or Subcontractor company name

            - A/E’s Seal (whoever prepared the drawing)

            - A Key Plan

        - Area of Work:  CAD drawings shall include a boundary that defines the area of work, showing only the area where work is performed.

      - BIM STANDARDS

          - Format

            - BIM models must be submitted in Revit .RVT format in a mutually agreed upon release.

          - Packaging for Submission

            - Models must be detached from central

            - All worksets must be relinquished

            - On final export dialog box, UNCHECK the box saying “Export views of sheets and links as external references.”

            - Use eTransmit to package model and related files.

          - File Names

            - Revit model file names must start with the UW PDG Project Number

      - CAD STANDARDS

          - Format

            - CAD files must be submitted in AutoCAD .dwg format.

          - File Organization

            - Each CAD drawing file must represent a single printed sheet.

          - File Names

            - Drawing and PDF file names must be titled <Sheet Number> <Sheet Name>.

              - Examples:   A-101 1ST FLOOR PLAN.dwg; A-101 1ST FLOOR PLAN.pdf

          - Image and .PDF References

            - Unreferenced and Unloaded images must be detached from the drawing.

              - No Unreferenced or Unloaded images or PDF underlays should appear in the Xref Manager

          - External References (XREFs)

            - External drawing references are not allowed.

            - External references used during the project must be bound using the ‘Bind’ option (instead of the ‘Insert’ option) before submitting.

      - PDF STANDARDS

        - Single Sheet .PDF

            - Each .PDF file must represent a single sheet and must not contain multiple pages.

        - File Names

            - .PDF file names must match the corresponding .DWG file names except for the file extension.

        - File Creation

            - .PDF files are to be created by printing from the native CAD/BIM format by printing to PDF.  Scanning is not permissible.

        - Layer Content

            - .PDF files must not contain layers.

        - Image Resolution (if applicable).

            - All documents must be created with a resolution of no less than 300 dpi.

        - Fonts

            - All fonts must be embedded in the .PDF.

        - Compression

            - When compression is used, the algorithm must be LZW, CITT Group 4, or PackBits.

        - Page Size

            - The .PDF page size must be the same as the original page size if the page were printed.

              - Example:  ANSI D sized sheet must have a .PDF sheet size of 22 x 34.

      - CAD Compliance Submittal Review Requirements:  CAD Shop Drawings shall be electronically submitted for Owner’s CAD compliance review and approval prior to submitting the final as-built Shop Drawings.  The Contractor may request a compliance review at any time during the work prior to Substantial Completion.  Refer to specification section 01 33 00.11 – “Submittal Standards Requirements and Compliance Review Exhibit” for electronic submittal formatting requirements.

  - OPERATIONS AND MAINTENANCE (O&M) MANUALS

    - The O&M Manuals shall contain all the information needed to operate, maintain and repair all systems, equipment, and product finishes provided in the Project.

    - Refer to specification section 01 78 23 – “Operation and Maintenance Data” for content, format, and submittal requirements of the O&M documentation including the electronic Operation and Maintenance (eO&M) documents.

    - The Contractor shall maintain the eO&M documentation throughout the construction and turnover phases of the project, up to the Final Completion submission of the O&M required to be provided just prior to final payment request by the Contractor.  During the closeout phase of the project, the Contractor shall be make two milestone submittals of the O&M documentation for review and approval.  The Contractor shall revise the documentation to incorporate all review comments.  The milestone submittals shall be as follows:

      - Substantial Completion Draft Submittal:  This submittal shall be in both print form and electronic form.  This submittal will be used as a review set by the A/E, Owner, and Commissioning Authority to ensure that the Contractor has prepared the documentation to be in compliance with the requirements of section 01 78 23 – “Operation and Maintenance Data” and is complete except for items that cannot yet be completed at the time of Substantial Completion for the project such as ongoing as-built drawings, etc.  However, all documentation required by the Contractor shall still be included in this review set, in their present state, even if they are not yet completed.

      - Final Completion Record Set Submittal:  This submittal shall be in both print form and electronic form.  This submittal shall be fully completed.  The Contractor shall use the Substantial Completion Draft submittal (electronic and printed versions) as the basis and update it for the Final Completion Submittal.  The Contractor shall clearly indicate what has changed from the Substantial Completion Draft Submittal.  The documents will be reviewed by the A/E, Owner, and Commissioning Authority for full compliance with the requirements of section 01 78 23.

    - The Contractor shall use eO&M version of the documents, in their current state, as a presentation reference for the demonstration and training activities.  The Contractor shall ensure that the eO&M documentation is complete for the materials presented at each training session that are associated with that session.

  - WARRANTIES AND BONDS MANUAL

    - Assemble executed warranties and bonds, and any certificates from the respective manufacturers, suppliers, and Subcontractors.  Provide preliminary review copies of all warranties and bonds and a final manual with the original documents, titled, “Warranties and Bonds Manual.”  Refer to specification section 01 78 36 – “Warranties” for requirements relating to content, formatting, and submittals of the warranties and bonds documentation.

  - DEMONSTRATION AND TRAINING

    - The Contractor shall provide on-site instruction, demonstration, and training for Owner's personnel in all aspects of the philosophy, operation and maintenance of equipment and systems.  Demonstration and training shall be provided by a qualified trainer from the Contractor or Subcontractor who supplied and installed the equipment and/or systems or a manufacturer's training representative who is familiar with all aspects of the design, operation, maintenance, and troubleshooting of the specified equipment and systems.  Training shall be conducted in a classroom setting with appropriate schematics, handouts, and audio/visual aids, as well as the most current documentation from the eO&M relating to the training topic.  All training shall be digitally recorded in video.  Attendance shall be recorded.  For work requiring commissioning, see Section 01 91 00 “General Commissioning Requirements” for further training session agenda requirements.

    - Refer to specification section 01 79 00 – “Demonstration and Training” for requirements relating to preparation of the Owner Training Plan, the types of training to be performed, training agenda submittals, training schedule, and training content and format.

  - CLEANING

    - Contractor clean up during construction is specified in the Contract Documents.

      - If Contractor fails to clean as specified in the Contract Documents, and after reasonable notice from Owner, Owner may do so and the cost thereof shall be charged to Contractor.

  - For work in medical centers, reference housekeeping in Section 01 35 33 “Infection Control.”

      - Contractor shall employ continuous housekeeping cleaning during construction to minimize interior construction dust and particulates during the Work.

    - Preliminary Cleaning:  Perform the following preliminary cleaning operations as a prerequisite for Owner’s Final Inspection.  Although the Contractor is responsible for this Work, the actual costs shall be included in the Division 02 through 49 subcontract bid packages.  The following are examples, without limitation, of minimum cleaning requirements:

      - Remove labels that are not permanent.

      - Remove temporary protective coatings and wrappings from all products.

      - Remove glazing compounds and other vision-obscuring substances from transparent and reflective materials provided by the Contractor including, but not limited to, mirrors, glass in doors and interior construction, glass canopies and skylights, and windows inside and out.

      - Clean all exposed building interior surfaces, including cabinet interiors, and new exterior surfaces to be free of foreign substances including, but not limited to, stains and films.

      - Leave floors broom-clean.  Vacuum carpeted surfaces and clean consistent with manufacturer’s recommendations for installation.

      - Remove and clean all construction debris and refuse from:

        - Roofs, mechanical and electrical rooms, tunnels and equipment vaults

        - Limited access spaces including above ceiling areas and shafts

        - Physically inaccessible components of the Work including wall and chase cavities, gutters and downspouts, floor drains and other drainage systems

      - Wipe surfaces of M&E equipment, including elevator equipment and similar Architectural equipment.  Remove excess lubrication and other substances.

      - Clean the Project site of construction waste, rubbish and litter.  Sweep paved areas broom clean and remove stains, spills, and other foreign deposits.

    - Final Cleaning:  Prior to Substantial Completion, employ experienced workers or professional cleaners for final cleaning of the Work.  Clean to a condition expected of a normal commercial building cleaning and maintenance program.  Comply with manufacturer's instructions.  Final cleaning is a negotiated support service.

      - Leave entire Project clean and ready for occupancy.  All new interior, including cabinet interiors, and exterior building surfaces, fixtures and equipment shall be turned over to the Owner in a new condition, free of all damage, dust, dirt, spots, stains, encrustations, and other blemishes.

      - Clean transparent materials including mirrors, glass in doors and interior construction, glass canopies and skylights, and windows inside and out.

      - Clean plumbing fixtures to a sanitary condition.

      - Clean light fixtures and lamps.

________________________________________________________________________________

Specifier – Custodial Services applies wax and sealers to most new floors on the UW Seattle campus.  Exceptions include the UWMC and Housing and Food Services projects.  Consult with UW Project Manager to determine which item 5 should be used.

      - Owner will wax and apply sealers to vinyl composition tile and sheet vinyl floors.

Or

5.	Apply floor finishes.

_________________________________________________________________________________

    - Compliance:  The Contractor shall:

      - Use non-toxic Green Seal Certified cleaning products, or products with low-volatile organic compounds (VOC), and cleaning paper with a post-consumer recycled content

      - Employ equipment with high efficiency particulate filtration and sweep compound to keep dust down

      - Comply with current regulations and standards of authorities having jurisdiction and the safety standards for cleaning specified in manufacturer’s instructions.

  - OWNER’S FINAL INSPECTION

    - Prior to Final Inspection:  The Contractor shall satisfactorily complete the following actions prior to the Owner’s final inspection of the Project.

      - Submit written notice that the Project is ready for final inspection.  Include a copy of the Contractor’s final punch list report (see Section 01 45 00 "Contractor Quality Control") and list all incomplete work items that have been reviewed with the Owner, and which the Owner has agreed are not necessary prior to Substantial Completion.

        - Include a written plan/schedule outlining all actions necessary to achieve Substantial Completion, without requiring extra ordinary participation by Owner and A/E.

      - Complete preliminary cleaning operations.

      - Submit the Owner Training Plan, including the completed training calendar, for Owner’s review and comment.

________________________________________________________________________________

Specifier – Delete any of the following items 4-8 not required by the Contract Documents.  Discuss with UW Project Manager

_________________________________________________________________________________

      - Replace all ventilation systems air filters specified for construction with final filters.

      - Complete start-up and functional performance testing of all systems required by the Contract Documents and AHJ including, but not limited to:  electrical testing; environmental control systems point-to-point testing; emergency eyewash and safety shower testing; fume hood face velocity testing; and HVAC air balancing.

      - Submit one (1) hard copy each of the current air balancing report and the M&E Commissioning Binders labeled “Preliminary,” listing all deficiencies, for Owner’s review and comment.

      - Submit the final copper and fiber optic communications cabling test results in PDF format, on Owner’s CMS.

      - Submit the final audio/visual equipment documentation including, but not limited to, manufacturer/model information and an itemized summary list with equipment serial numbers in PDF format, on Owner’s CMS.

    - Owner’s Final Inspection:  Upon satisfactory completion of the actions in 1.7A, Owner will determine if the Project is complete and ready for final inspection and, at Owner’s sole discretion, commence final inspection, or provide a written deficiency list of items to the Contractor of work that must be completed to the satisfaction of the Owner prior to Owner’s final inspection.  Final inspection is performed by the A/E and Owner’s representatives.

      - After the Owner has issued the final inspection list of corrective work items, the Contractor shall make the required corrections and/or identify items that the Contractor feels are not required by the Contract Documents, and resolve these items with the Owner.

    - Re-inspection:  Contractor shall request, in writing, re-inspection after completing the Owner’s final inspection list of corrective work items and providing the Owner the final inspection report notated with a signed-off approval for each of the corrected items.  Those items whose completion is delayed due to circumstances acceptable to the Owner will be exceptions.  The Owner’s Representative will back check the items or have the A/E perform a re-inspection.

      - If the A/E is required to perform more than one re-inspection, the costs for additional inspections may be borne by the Contractor, at the Owner’s sole discretion.

  - SUBSTANTIAL COMPLETION

    - Substantial Completion:  Substantial Completion (for either the entire Work or portions thereof) shall be achieved when all Work, other than incidental corrective and incidental punch list work, is complete including, but not limited to, the following actions:

      - Complete final cleaning operations.

      - Submit the "Substantial Completion Draft Submittal" of the operations and maintenance data for Owner’s review and comment in one (1) hard copy and in the required eO&M format.

      - Submit all sign-offs, releases, jurisdictional settlements, judgments, and other records from AHJ allowing the Owner’s full and unrestricted use and benefit of the facilities including, but not limited to, a temporary or permanent certificate of occupancy permit, operating permits and/or licenses for the use of building equipment such as elevators, boilers, paint booths, etc. and similar necessary certificates and releases.

        - Provide a list of any outstanding work required by AHJ.

      - Submit the current As-Built Drawings and Specifications identified “Preliminary” As-Built (marked with the date of submission) in the required eO&M Substantial Completion Draft Submittal.

      - Submit the As-Built Shop Drawings required by the Contract Documents and, when specified, the BIM in accordance with this Section 1.2D.5, in the required eO&M Substantial Completion Draft Submittal.

      - Remove all construction tools and temporary facilities not required for Final Completion work from the Project site including, but not limited to, storage sheds, samples and mock-ups, Project identification signage, site fences, crane and hoist base foundation construction, temporary enclosures, and construction electrical power and service.

      - Complete Owner’s personnel demonstration and training and submit video files in the required eO&M Substantial Completion Draft Submittal.

__________________________________________________________________________________

Specifier – Discuss with UW Project Manager and delete any of the following items 8-12 not required by the Contract Documents.

__________________________________________________________________________________

      - Deliver specified maintenance equipment and tools to Owner, with itemized summary list.

      - Complete final change-over of locks, transmit new keys to Owner, and return Owner’s loaned construction keys.

      - Complete all air balancing, testing and commissioning work required by the Contract Documents, allowing the Owner to fully occupy the Work for the use for which it is intended.  Incidental Work, that is not life safety or occupational safety commissioning work, whose completion is delayed due to circumstances excused by the Owner, will be the exception.

  - Submit one (1) hard copy each of the current air balancing report and M&E Commissioning Binders (marked with the date of submission) noting the corrections for deficiencies listed in the “Preliminary” report and binders and indicating any incomplete Work.

      - Submit all controls systems software files required by the Contract Documents including, but not limited to, lighting and environmental controls.

      - Submit one (1) hard copy of the current Build It LEED Toolkit ® with all LEED documentation labeled “Preliminary,” for Owner’s review and comment.

    - Substantial Completion:  Upon a satisfactory completion of the actions in 1.8A above and the General Conditions requirements for Substantial Completion, the Owner will prepare a letter of Substantial Completion and forward to Contractor.  The letter will identify the date of Substantial Completion and include the final punch list report and the commissioning deficiencies list, listing all remaining incomplete work.  Contract warranties will begin as of the date of Substantial Completion, as specified in Section 01 78 36 “Warranties,” or as otherwise indicated in the Contract Documents.

      - Substantial Completion and the start of warranties for incomplete items will be established in writing by the Owner when the item is determined complete.

  - FINAL COMPLETION

    - Prior to Final Completion:  Final Completion shall be achieved when the Work is fully and finally complete, to the Owner’s satisfaction in accordance with the Contract Documents including, but not limited to, the following:

      - All Work, including incidental corrective or punch list work, and air balancing and commissioning work (if included in the scope of the Work) is complete and correct to the satisfaction of the Owner.

      - All remaining temporary facilities are removed from the Project site and the site (including landscape) is restored to original conditions or Contract Documents requirements.

      - All final permits, originally issued as temporary permits, have been submitted.

      - The final marked-up As-Built Drawings and Specifications identified Final As-Built (marked with the date of submission) have been submitted in hard copy; and in the eO&M Final Completion Record Set Submittal.

      - The complete operations and maintenance data has been submitted in hard copy and in the eO&M Final Completion Record Set Submittal.

      - A separate, bound hard copy of the Warranties and Bonds Manual, with original documents, has been submitted.

      - The Contractor’s final 3-ring binder of all MSDS used for construction, marked with the date of submission, has been submitted in PDF format, on Owner’s CMS.

      - The Contractor’s final cumulative Construction Waste Management Report (marked with the date of submission) has been submitted in PDF format, on Owner’s CMS.

      - All Change Orders are approved and signed by both parties.

      - A draft of the Final Application for Payment has been submitted to Owner for review and approval.

      - The final Schedule of Values and the Building Componentization Report in hard and electronic copies (see Section 01 29 76 “Progress Payment Procedures”) have been submitted.

_________________________________________________________________________________

Specifier –  Delete any of the following items 11-16 not required by the Contract Documents.  Discuss with UW Project Manager

_________________________________________________________________________________

      - The final air balancing report and the final M&E Commissioning Binders (marked with the date of submission) have been submitted in PDF format, on Owner’s CMS.

        - For Projects with a Test Engineer, the as-built information updating the A/E commissioning basis-of-design has been submitted with the Commissioning Binders.

      - The software file used to calculate the power systems studies (Power Tools – SKM ®) has been submitted.

      - Specified spare parts, extra stock of materials, and extra materials of value to the Owner, with itemized summary list, have been submitted.

      - The “Regulated Materials – Waste Manifests” (marked with date of submission) have been submitted in PDF format, on Owner’s CMS.

      - For Projects at the University of Washington Medical Centers, all personnel identification badges have been returned.

      - All required USGBC LEED certification on-line forms are submitted and the final Build It LEED Toolkit ® with all final LEED documentation including the LEED estimated construction costs have been submitted in PDF format, on Owner’s CMS.

    - Final Completion:  Upon satisfactorily completion of the requirements in 1.9A above to achieve Final Completion, the Owner will approve and process the final Application for Payment and establish the date of Final Completion thereon.

  - FINAL ACCEPTANCE

    - Final Application for Payment has been approved by Owner and payment made to the Contractor.

    - The Owner will establish the date of Final Acceptance and issue the letter of Final Acceptance after the Contractor has completed the requirements of the Contract Documents.

      - The Contractor shall follow the requirements outlined in the General Conditions and Section 01 29 76 “Progress Payment Procedures” for release of retainage.

PART 2 - PRODUCTS (Not Used)

PART 3 - EXECUTION (Not Used)

END OF SECTION