# ATTACHMENT B

# 0A1 Agreements with the University of Washington

# DESIGN AND CONSTRUCTION DOCUMENTS REQUIREMENTS

This Attachment B to the Agreement for the above-referenced Project designates the specific design documents and deliverables required for University review, including items set forth in the Owner’s departmental Design Guides.  The list is not all inclusive and is not intended as a limitation on services described in the Agreement.

Basic Services:  Documents and deliverables required under Article II of the Agreement are marked in the Basic Services column.  Sub-items listed and noted by a double dash (--) may not all be applicable to all projects and are listed as examples of the deliverables that must be reviewed prior to the completion of Construction Documents.

Additional Services:  Attachment B also specifies whether items are required and payable as Additional Services in accordance with the provisions of Article II and Article III of the Conditions of the Agreement and any Special Conditions made a part of this Agreement.  Additional Services will be authorized separately from Basic Services.  Other Additional Services not specified in this Attachment B may be added as appropriate and necessary during the term of the Agreement.  Sub-items listed and noted by a double dash (--) may not all be applicable to all projects and are listed as examples of the deliverables that must be reviewed prior to the completion of Construction Documents.

Instructions to CPO Project Manager

- Highlighted boxes indicate services identified in the A/E Agreement and in the Office of Financial Management, Capital Budget Instructions as Basic Services or Additional Services when using the State Fee Schedule for determining A/E fees.  Highlighting is provided as a guide only, in order to facilitate consistency of A/E negotiations.  When negotiations are complete, and the Attachment is ready for inclusion in the final Agreement, the Project Manager may disable the highlighting for all boxes.

- The Basic Services boxes pre-marked with an ( apply to all Projects and should not be changed.  Other Basic Services shall be marked as applicable.

- The Additional Services boxes the Project Manager marks with an ( are agreed to be required for the Project and the fees for these services shall be negotiated and authorized separate from the Basic Services fees.

- When complete, fill in the Project Name and Number in the Header, delete these highlighted instructions, and forward to the Contracts Office for inclusion in the A/E Agreement.

- NOTE:  if a heading or item is not marked it is not a requirement of the Agreement.

| Headings and Items | Basic Services | Additional Services | Schematic Design Phase |
| --- | --- | --- | --- |
| Computer Aided Design Files (CAD files) | ( | ( | Provide a representative electronic CAD drawing sample from A/E, and each A/E sub-consultant, for Owner’s CAD standards/format review. |
|  | ( | ( | Provide electronic floor plan(s) / room numbers showing the proposed numbering methodology, for Owner’s CAD standards review. |
| Codes, Laws, and Policies | ( | ( | Narrative summary of the Seattle Campus Master Plan requirements: --Campus policies, goals and objectives, development program, and standards for the Project. |
|  | ( | ( | Code analysis design narrative: --Building Code; Fire Code; NFPA (for medical facilities) --Owner’s Americans with Disabilities Act (ADA) requirements --Energy Code requirements and development standards --laboratory control zones --egress atrium fire protection --identify any planned use of Code alternates or variances |
|  | ( | ( | Provide environmental mitigation documentation, required by the State Environmental Policy Act (SEPA) as a condition of the Project. |
|  | ( | ( | Zoning Study |
| Safe Design Provisions | ( | ( | Project specific design hazards analysis narrative. |
| Sustainable Design | ( | ( | Capital Projects Office “SustainAbilities Scorecard” |
|  | ( | ( | Preliminary US Green Building Council “Leadership in Energy and Design” (USGBC “LEED”) scorecard with summary narrative. |
|  |  |  | Completed LEED “Project Summary”. |
|  | ( | ( | For state funded projects, completed Washington State Department of General Administration “Environmental Design Considerations” form. |
| Acoustics | ( | ( | Noise criteria design narrative scope description: --occupied space(s) and Mechanical & Electrical (M&E) requirements --vibration isolation requirements --for labs see http://www.ehs.washington.edu/fsodesignrev/1f-rwdi.pdf |
| Temporary Construction Facilities | ( | ( | Temporary construction facilities concept narrative. |
|  | ( | ( | Infection control concepts narrative (medical facilities projects). |
| Demolition | ( | ( | Design narrative scope description for each demolition component: --elements to be salvaged or protected |
|  | ( | ( | Preliminary demolition diagrams showing new and existing: -- service continuity concept for impacted occupied building facilities |

| Civil | ( | ( | Design narrative scope description: -- define systems and systems materials --constructability considerations and impacts due to utility shutdowns. |
| --- | --- | --- | --- |
|  | ( | ( | Preliminary new utilities load calculations. |
|  | ( | ( | Document existing Site features with new conditions: --Project footprint with dimensions --preliminary grading and contours / retaining walls --concrete and asphalt hard surfaces --utility connections and routings (coordinate existing utilities and tunnels including vaults & duct banks) |
|  | ( | ( | City Right-of-Way improvements concept. |
|  | ( | ( | Confirm availability and capacities of existing utilities (including fire water supply) and coordinate / M&E design narrative. |
| Utility Tunnels and Vaults | ( | ( | Design narrative scope description indicating utilities connected to Campus systems and utility materials. |
| Site Improvements | ( | ( | Design narrative scope description: --bicycle parking requirements (ref: Transportation Services - Programming Issues Design Guide) --soils management, replacement, or enhancement requirements --Crime Prevention through Environmental Design (CPTED) considerations including “code blue” phone requirements --site furnishings |
|  | ( | ( | Site Plan with proposed conditions: --roads, parking lots, and emergency vehicle access routes --pathways and ADA access routes --bicycle provisions --coordinate Site lighting , hard surfaces, and landscaping concepts --identify LEED “Site boundary” |
| Landscaping and Irrigation | ( | ( | Completed Campus Tree Evaluation Report. |
|  | ( | ( | Conceptual planting plan indicating types, sizes, and location of vegetation (including removed, replaced, protected, and salvaged). |
|  | ( | ( | Conceptual irrigation plan identifying irrigation area, types of irrigation, and irrigation water point-of-service. |
| Building Enclosure | ( | ( | Building envelope design narrative / performance criteria validating the compatibilities of the proposed thermal and moisture control protection systems (cladding, curtain wall, roofing, foundations, and plazas). |
|  | ( | ( | Preliminary details of cladding, curtain wall, roofing, and plaza thermal and moisture control protection systems. |
|  | ( | ( | Elevations @ 1/8” scale minimum showing fenestration layout, materials designations, and indication of air intake and exhaust locations. |
|  | ( | ( | Building cross-sections. |
|  | ( | ( | Roof plan / major appurtenances including roof equipment & skylights. |
| Signage | ( | ( | Way finding & code signage design narrative scope description. |

| Building: Interior | ( | ( | Design narrative scope description, Divisions 6, and 8 thru 11. |
| --- | --- | --- | --- |
|  | ( | ( | Floor plans / doors @ 1/8" scale minimum showing: all program and support space locations (with their floor-to-floor relationships); fire rated and structural partitions; preliminary interior relite concepts; casework and fixed equipment; and future expansion and/or addition provisions. Support spaces include, but are not limited to: --custodial, recycling, and mailrooms (http://www.washington.edu/facilities/engr/fsdg/04_Architectural/19-11F_BuildingMaintenance.pdf) --electrical rooms and closets (http://www.washington.edu/facilities/engr/fsdg/16_Electrical/06-16E_BuildingPowerDistribution.pdf) |
|  |  |  | --Router Rooms (RR), Main Distribution Frame (MDF), and Intermediate Distribution Frame (IDF) communications rooms (http://www.washington.edu/admin/facilities/pfi/fdi.html) --CAAMS rooms (ref: CAAMS in this Attachment B) --toilet rooms --mechanical shafts and chases --stairs, elevators and elevator rooms --loading dock facilities --penthouses and M&E rooms (indicate concepts for equipment access and replacement provisions) --HVAC environmental control room (http://www.washington.edu/facilities/engr/fsdg/15_Mechanical/33-15R_EnvironmentalControlSystems.pdf) |
|  | ( | ( | Preliminary layouts of major Project spaces, including but not limited to, offices, laboratories, medical and classroom spaces at 1/4" scale min. |
|  | ( | ( | Typical reflected ceiling plan(s) @ 1/8” scale minimum. |
|  | ( | ( | Net-to-gross area tabulations compared to Program. |
| Laboratory Facilities | ( | ( | Design narrative scope description of each laboratory considering the requirements of the EH&S Laboratory Safety Design Guide: --identify laboratory types (BL 1 - 4) and hazardous “H” occupancies |
|  | ( | ( | Preliminary plan layouts / doors showing: --casework and fixed equipment, including safety equipment |
| General Use Classrooms | ( | ( | Design narrative scope description considering the requirements of the Classroom Support Services - General Use Classrooms Design Guide. |
|  | ( | ( | Plans / elevations indicating concept and configuration of classrooms: --show columns and intrusions into functional room space. |
| Loading Dock Facilities | ( | ( | Design narrative scope description considering the requirements of the Transportation Services – Programming Issues Design Guide and the Facilities Services – Design Guidelines for Recycling and Solid Waste. |
|  | ( | ( | Conceptual loading dock plan: --truck maneuvering requirements (ref: Civil in this Attachment B) --stall types, platform heights, dock access (ramps, stairs, ladders) --dumpsters and totes |
| Elevator(s) | ( | ( | Elevator(s) design narrative scope description: --numbers of cars and speed --elevator cab sizes and capacities --elevator controls requirements --UW-IT phone unit type and installation / access criteria |
|  | ( | ( | For new construction, submit a traffic study. |

| Structural | ( | ( | Design narrative scope description: --floor and roof loads --floor flatness and levelness criteria --structure borne vibration criteria --exterior facade support concept |
| --- | --- | --- | --- |
|  | ( | ( | For renovations, seismic analysis / proposed strengthening concepts. |
|  | ( | ( | Floor and/or roof framing plans: --foundations --floor-to-floor heights --locate seismic joints --indicate piles |
|  |  |  | Legend |
| Refrigeration: Computer Server and Cold Rooms (Environmental Rooms) | ( | ( | Design narrative scope description / design criteria: --provide responses to the FSDG programming questions http://www.washington.edu/facilities/engr/fsdg/15_Mechanical/31-15P_Cold-EnvironmentalRooms.pdf --monitoring requirements (including refrigerant leak detection & alarm) |
|  |  |  | Show rooms and equipment locations on Mechanical Plans |
| Plumbing potable and non-potable, acid and laboratory waste, waste and drains, compressed air, vacuum, nitrogen, natural gas, and RO/DI | ( | ( | Design narrative scope description with systems criteria: --pump design criteria --identify all special occupancy zones and systems requiring special plumbing (e.g. tempered water for emergency fixtures) --provide toilet room fixture count calculations |
|  | ( | ( | Preliminary design calculations (indicate energy balances): --provide total estimated water consumption calculations for new buildings, major renovations, and landscaping --provide the estimated use-volumes of all plumbing services (e.g. water, compressed air, natural gas) |
|  | ( | ( | Piping plans and diagrams: --indicate pipe risers, pipe headers, pipe chases, plumbing equipment, utility connections, backflow prevention, and plumbing fixtures --identify the concept of horizontal pipe runs |
|  |  |  | Legend |
|  | ( | ( | Preliminary one-line systems riser diagrams: --identify system coils --locate meters |
|  | ( | ( | For Compressed Air, Vacuum, Natural Gas, Nitrogen, and/or RO/DI show: a block layout of the central equipment, pressure reducing stations and pipe headers, and the concept of outlet connections. |
| Fire Protection | ( | ( | Design narrative scope description: --hazard classification --suppression systems special conditions |
|  | ( | ( | Floor plans showing: --connection to utility and backflow prevention location --supply and cross mains routings --standpipe locations |

| HVAC Piping process and environmental chilled water, central cooling water, steam and condensate, and hydronic heating | ( | ( | Design narrative scope description with systems criteria: --identify all special occupancy zones and systems requiring process chilled water --room temperature set-points |
| --- | --- | --- | --- |
|  | ( | ( | Preliminary design calculations (indicate energy balances): --total estimated water consumption calculations for new buildings and major renovations --estimated use of utility resources (steam, central cooling water) |
|  | ( | ( | HVAC piping plans: --indicate pipe risers, pipe headers, pipe chases, HVAC equipment, and utility connections --identify the concept of horizontal pipe runs --locate process chilled water cooling towers and chillers |
|  |  |  | Legend |
|  | ( | ( | Preliminary one-line systems diagrams: --identify system coils --locate meters |
| HVAC | ( | ( | Design narrative scope description: --strategy for zoning air distribution systems considering usage and occupancy (identify special occupancy rooms and zones) --room air change requirements, for labs see http://www.ehs.washington.edu/fsodesignrev/1a-rwdi.pdf --smoke control requirements and concepts --pressurization fans design concept --types of fume hood exhaust and control systems --special exhaust systems --for retrofit projects, existing systems to be altered --all systems filters and coils --identify: Minimum Efficiency Report Value (MERV) filtration media during construction (temporary) and for final occupancy (permanent), and moisture and dust protection measures required for construction |
|  | ( | ( | Preliminary design calculations: --air handlers, ventilation fans, and air intakes |
|  | ( | ( | HVAC single line duct layout plans: --all systems fans and motors --quantity and location of motors requiring Variable Frequency Drives --shafts and horizontal duct distribution concepts --supply and exhaust point(s)-of-connection for renovations, or air intake and exhaust location(s) / size for new construction (indicate location of cooling tower exhaust(s) relative to the air intake) |
|  | ( | ( | Preliminary one-line systems flow and riser diagrams. |
|  | ( | ( | For mechanical systems air intakes and exhausts, provide environmental air quality study. http://www.ehs.washington.edu/fsodesignrev/1d-rwdi.pdf |
| Environmental Controls | ( | ( | Design narrative scope description: --controls system strategy |
| Commissioning and TAB Testing, Adjusting, and Balancing | ( | ( | Design narrative scope description with list of systems and equipment to be commissioned: --Seattle Department of Planning & Development (DPD) requirements --Mechanical - TAB activities, for new and existing systems (including those required prior to demolition-renovation of existing systems) --Electrical - inspection, calibration, and testing requirements |
| Audio Visual (AV) | ( | ( | Technology design narrative scope description for general use classrooms, departmental-owned classrooms, and other learning spaces, including teaching laboratories. |

| Electrical: Primary Distribution | ( | ( | Design narrative scope description: --connections to the Campus primary distribution system / routing --work related to utility tunnels and vaults, manholes, and ductbanks |
| --- | --- | --- | --- |
|  | ( | ( | Preliminary one-line diagram. |
| Medium Voltage Switchgear | ( | ( | Design narrative scope description: --proposed equipment location / preliminary equipment sizes --power ratings --connection arrangement (ring bus, preferred / alternate) |
| Load Interrupter Switches | ( | ( | Design narrative scope description: --location and service arrangement |
| Emergency Power and ATS | ( | ( | Design narrative scope description: --emergency power provisions and source of emergency power --National Electric Code (NEC) emergency power branches --Automatic Transfer Switch (ATS) styles & requirements --Central Monitoring and Control System (CMCS) equipment / preliminary In-put/Out-put (IO) points |
|  | ( | ( | Preliminary load estimate. |
|  | ( | ( | Plans showing proposed generator, ATS, and equipment locations. |
|  |  |  | Preliminary one-line diagram including all equipment. |
| Electrical: Building Services | ( | ( | Design narrative scope description: --building service type --service operability and maintainability |
|  | ( | ( | Preliminary electrical room layout @ 1/4” scale minimum: --identify equipment replacement considerations |
|  |  |  | Preliminary one-line diagram including all equipment. |
| Transformers | ( | ( | Design narrative scope description: --quantity, size, and equipment rating base on preliminary load estimates |
| Switchboards and Panelboards | ( | ( | Design narrative scope description: --power distribution concept and required equipment --identify watts/square foot value of anticipated loads |
| Monitoring and Metering | ( | ( | Design narrative scope description for the Energy Monitoring and Management System (EMMS): --preliminary list of monitoring points and types of metering |
| Motor Control Centers (MCCs) and VFDs | ( | ( | Design narrative scope description: --identification of motors requiring VFDs to be served from MCCs |
|  |  |  | Plans showing the proposed equipment location. |
| Building Power Distribution and Power Quality | ( | ( | Design narrative scope description: --power distribution concept with point-of-service, and for existing systems, modifications to existing systems --power quality requirements --Electronic Magnetic Field (EMF) and noise sources mitigation |
|  | ( | ( | Preliminary load estimate. |
| Electrical: Grounding | ( | ( | Design narrative scope description of systems requiring grounding. |
| Electrical: Raceways | ( | ( | Design narrative scope description: --raceway systems |
| Electrical: Wire, Cable, and Terminations | ( | ( | Design narrative scope description: --materials and terminating devices --distribution concept |
| Electrical: Wiring Devices | ( | ( | Design narrative scope description: --identify special requirements (hospitals and laboratories) |
| Power System Studies | ( | ( | Identify fault value assumptions on existing systems that will be used for the preliminary short circuit study. |

| Lighting | ( | ( | Design narrative scope description /control concepts: --lighting control designs being considered / day lighting plans --preliminary light fixture quality definition --preliminary Site lighting (ref: Site Improvements in this Attachment B) |
| --- | --- | --- | --- |
|  |  |  | Zone (room) foot candle schedules: --consider special conditions (e.g. sloped-floor classrooms) |
| Clock and Bell | ( | ( | Preliminary riser diagram. |
| Miscellaneous Signal Systems | ( | ( | Design narrative scope description concepts for each system including, but not limited to: nurse call, intercom, public address, and alarms / remote monitoring. --indicate points-of-service and service size space requirements |
| Fire Alarm | ( | ( | Design narrative scope description: --systems definition and unique criteria |
|  | ( | ( | For retrofit projects, provide field audibility study. |
|  | ( | ( | Plans showing: --terminal cabinet locations and main conduit routing --Fire Alarm Control Panel (FACP) and annunciator locations --for new projects, connection to public utility or Campus fire alarm reporting system |
| Campus Automated Access Management System (CAAMS) | ( | ( | Design narrative scope description: --identify controlled openings (interior and exterior) --define head-end backboard room size and indicate location) --summarize responsibilities of A/E and Owner’s CAAMS Contractor |
| Closed Circuit TV (CCTV) | ( | ( | Design narrative scope description: --indicate head-end location and approximate number of cameras |
| User Information Technologies | ( | ( | Design narrative scope description for user computer rooms and computer labs / sizes and M&E requirements. |
| Communications: Infrastructure Voice & Data / WIFI / CATV / IRS | ( | ( | Design narrative scope description for each service: |
|  |  |  | --conduit, boxes, and SMR / densities --horizontal and station pathways --demolition of existing systems & impacts on areas to remain in service |
|  | ( | ( | Indicate on the Electrical plans: --MDF and IDF rooms showing pathway interconnections --preliminary cable tray routing --service distances over 90 meters --for outside “Site” installations, pathway / point-of-service connection --for building / utility tunnel installations, entrance pathway route and size |
|  |  |  | MDF/IDF Analysis Worksheet in 8 ½” x 11” format. |
|  |  |  | Classroom Functional Use Analysis Worksheet in 8 ½” x 11” format. |
|  | ( | ( | One-line riser diagrams: --pathways with quantities and sizes |
| Communications: Cable Plant Voice & Data / WIFI / CATV / IRS | ( | ( | Design narrative scope description for each service: --identify UW Husky TV vs. satellite CATV --SM fiber optic, copper, and coax cables requirements --cable plant for riser and stations --requirement for racks and universal cable plant --approximate number of cabled outlets --outlet densities with termination requirements --testing requirements |
|  | ( | ( | Internal Re-Radiating System (IRS) design narrative scope description. |

End of Attachment B – Schematic Design Deliverables

| Headings and Items | Basic Services | Additional Services | Design Development Phase |
| --- | --- | --- | --- |
| CAD Files | ( | ( | Provide a representative electronic CAD drawing sample from A/E, and each A/E sub-consultant, for Owner’s CAD standards/format review. |
|  | ( | ( | Provide an electronic submittal of all floor plans with room numbers, for Owner’s CAD standards/room numbering review. |
|  | ( | ( | For all projects with wireless communications, provide three (3) CD/DVDs of the floor plans layered for Owner’s use. |
| Codes, Laws, and Policies | ( | ( | Developed code analysis design narrative / design documentation. |
|  | ( | ( | Document mitigations compliance required by SEPA conditions. |
|  | ( | ( | Submit Master Use Permit (MUP) documentation to AHJ: --show zoning compliance, including building height calculations |
| Safe Design Provisions | ( | ( | Developed design hazards analysis narrative with plans and details showing, but not limited to, mitigations for noise, slippery surfaces, tripping hazards, falling objects, confined space, ergonomics. (ref: EH&S “Safe Access and Fall Protection” design guide) |
| Sustainable Design | ( | ( | Updated CPO “SustainAbilities Scorecard”. |
|  | ( | ( | Final USGBC LEED scorecard with a 1 to 3 page narrative of the strategies used to achieve LEED credits. |
| Project Manual and Calculations | ( | ( | Project specific outline Specifications / developed narratives --indicate proposed products and materials --define Owner’s door hardware requirements --seismic performance design requirements for nonstructural systems |
|  |  |  | List of proposed proprietary bid items, by Specification Section. |
|  | ( | ( | List of proposed Contractor submittals, including but not limited to: materials, equipment, and Shop Drawings, by Specification Section. |
|  | ( | ( | Matrix list of tests and inspections required, by Specification Section. |
| Materials and Colors | ( | ( | Proposed samples of finish materials / color selections and maintenance information. |
| Temporary Construction Facilities | ( | ( | Temporary construction facilities plans: --site fences, temporary enclosures, barriers, tree protection --pedestrian bypass and egress routes / exit signage locations. --access thru Owner’s facilities including use of Owner’s elevators --construction trailers and contractor parking provisions --dumpsters, tower crane, and hoisting locations --street use and construction vehicle Site access --show construction utilities point-of-service |
|  | ( | ( | Infection control plans / details (medical facilities projects). |
| Demolition | ( | ( | Developed demolition plans / proposed details: --Civil, M&E, and Communications services points-of-terminations --elements to be salvaged or protected |

| Civil | ( | ( | Developed design narrative: --vehicular load design requirements --acceptance test requirements --fire hydrant flushing requirements and hydrant restraints |
| --- | --- | --- | --- |
|  | ( | ( | New utilities load calculations. |
|  | ( | ( | Storm water discharge downstream report. |
|  | ( | ( | Developed site plan with University coordinates: --Project footprint with dimensions --elevations of all edges and breaks --grades and contours / retaining walls --concrete and asphalt hard surfaces / cross sections, slopes, and curbs --parking and loading docks / vehicle maneuvering diagrams --utilities with routes, pipe sizes, inverts, elevations, slopes, connections, building penetrations, manholes, catch basins, cleanouts, meters, and fire (pump truck) connection. (coordinate existing utilities and tunnels including vaults & duct banks) --trenches and excavations |
|  |  |  | Proposed details: --catch basins and cleanouts / grates and covers --thrust blocks (including area), and thrust rods (including diameter) --manhole plans and sections / inlet and outlet elevations --valves, hydrants, supports, connections, and joints |
|  | ( | ( | Edit FSDG “Earthwork” guide specification customized for Project. |
|  | ( | ( | City Right-of-Way improvements. |
|  | ( | ( | Shoring concepts and member sizes. |
|  | ( | ( | Erosion and Sedimentation Control Plan, for new construction. |
| Utility Tunnels and Vaults | ( | ( | Plans, sections / profiles, and proposed details showing: materials, tunnel drains, vaults / top layout and equipment sizes / catalog numbers, utility entrance locations, splices, and details of supports, connections, joints, grounding, penetrations, and pipe and cable racking. |
| Site Improvements | ( | ( | Site plan with developed conditions showing: --roads, parking lots, loading docks, Physical Plant and ADA parking, and Dial-A-Ride shuttle stops with paint stripping -- stairs, walkways, and curb cuts & ramps showing ADA access routes --bicycle racks, covered rack structures, and bicycle lockers --soils management, replacement, or enhancement provisions --Site finishes and furnishings --“code blue” phones, site lighting, retaining walls and plazas --identify LEED “Site boundary” |
| Landscaping and Irrigation | ( | ( | Developed planting plan. |
|  |  |  | Proposed details: --tree pit / dimensions, guying, and protection. |
|  | ( | ( | Schedule of trees to be removed / appraised value & salvage potential. |
|  | ( | ( | Irrigation plan showing types of irrigation, main line sizing and layout, point-of-service, and controller and header / vault locations. |

| Building Enclosure | ( | ( | Elevations @ 1/8” scale minimum showing: --material designations, fixed and operable window sash locations, and louvers and air intake and exhaust locations. |
| --- | --- | --- | --- |
|  | ( | ( | Building cross-sections. |
|  | ( | ( | Wall sections with details at intersections of systems: --masonry penetrations, soft joint and support locations --doors and windows --wall systems and thru wall flashing --seismic and building joints |
|  | ( | ( | Roof plans showing all appurtenances with typical details: --roof slopes and edge conditions --drains, scuppers, curbs and flashings, walking protection, skylights, ladders and stairs, fall protection anchors, and roof equipment. |
|  | ( | ( | On-structure details of Site construction including planters, pavers, stairs and ramps showing waterproofing, slopes and drains. |
| Building Interior | ( | ( | Floor plans / doors @ 1/8" scale minimum showing: --room numbers --casework, fixed equipment and fixed seating --walls / openings showing types and ratings (indicate structural walls) --marker boards, tack boards, signage, window coverings --fire extinguishers and extinguisher cabinets locations --mechanical shafts and chases |
|  |  |  | Room finishes schedules / finishes placement drawings. |
|  |  |  | Proposed details: --ADA, millwork, walls --door, door frames / door hardware (coordinate with CAAMS in this Attachment B) |
|  | ( | ( | Reflected ceiling plans @ 1/8” scale minimum showing: --ceiling and soffit heights and ceiling types --lighting, diffusers, maintenance access requirements, and fire sprinkler locations at laboratories and architectural feature spaces --ceiling-hung AV equipment including data projectors, sound speakers, and projection screens |
|  |  |  | Sections at congested M&E ceiling areas @ 1/2" scale minimum: --show M&E systems and cable tray access requirements/clearances |
|  | ( | ( | All Project spaces, including but not limited to, offices, laboratories, and medical and classroom spaces @ 1/4" scale minimum showing: --fixed and movable equipment and fixed seating --aisle widths, columns and intrusions into functional room space --casework, shelving, specialties |
|  | ( | ( | Interior elevations of public spaces. |
|  | ( | ( | Door type, door hardware, and relite schedules, with fire ratings |
|  | ( | ( | Net-to-gross area tabulations compared to Schematic Phase. |
|  | ( | ( | Edit EH&S “Fire Extinguishers and Cabinets" guide specification customized for Project |
| Equipment and Furnishings | ( | ( | Contractor furnished and Contractor installed (CFCI) fixed equipment selections and cut sheets. |
|  | ( | ( | Owner furnished and Contractor installed (OFCI) equipment and/or furniture design and coordination plans. |

| Signage | ( | ( | Code signage placement plans and details including room signs, occupancy signs, and evacuation signage. |
| --- | --- | --- | --- |
|  | ( | ( | Way-finding signage placement plans, graphics, and details. |
| Laboratory Facilities | ( | ( | Detailed plan layouts / doors showing: --safety equipment, laboratory signage locations (emergency showers / code required clearances from obstructions) --identify fume hoods, bio-safety cabinets, and flammable storage cabinets by types, brands, and model numbers --fume hood and HVAC diffuser locations http://www.ehs.washington.edu/fsodesignrev/1c-rwdi.pdf |
|  | ( | ( | Enlarged laboratory casework systems / sections and elevations. |
|  | ( | ( | Edit EH&S “Laboratory Fume Hoods” guide specification customized for Project. |
|  | ( | ( | For projects in the Health Science Center, edit the HSC “Laboratory Casework” guide specification customized for Project. |
| General Use Classrooms | ( | ( | Plans and elevations / details showing the complete design: --furniture layouts with ADA and other code requirements --AV equipment and support equipment, locations and controls --special systems, including multi-media and sound systems --lighting, lighting controls, electrical receptacles |
| Loading Dock Facilities | ( | ( | Developed loading dock plan / details showing: --stall types, platform heights, dock access (ramps, stairs, ladders) --dock levelers and scissor lifts, indicating load capacities --cranes and hoists, indicating models and capacities --dock bumpers and safety paint stripping --indicate air lock concept to isolate truck odors from building interior. |
| Elevators(s) | ( | ( | Car plan(s) / interior elevations and reflected ceiling plan @ 1/4” scale minimum showing dimensioned phone cabinet and controls location |
|  |  |  | Hall elevations / hall buttons and car and hall position indicators: --identify key box location |
|  |  |  | Door and frame details |
|  |  |  | Edit FSDG “Elevators” guide specification customized for Project: --coordinate phone and CAAMS |
|  | ( | ( | Elevator shaft plans and sections @ 1/4” scale minimum: --show shaft venting and/or pressurization |
| Structural | ( | ( | Calculations |
|  | ( | ( | Floor and roof framing plans / details: --main member sizing --rebar sizes and quantity --major beam penetrations --dimensioned floor penetrations, curbs, and depressions --cambers and slopes --construction, seismic, and control joints --lateral system defined --concrete wall thicknesses |
|  |  |  | Legend |
|  | ( | ( | Foundation plan / details: --penetrations, footing sizes and pile sizes / locations |
|  | ( | ( | Wall sections / floor-to-floor heights and details: --exterior facade support concept |
|  | ( | ( | Concrete design mix with curing methods and placement criteria. |

| Refrigeration: Computer Server and Cold Rooms (Environmental Rooms) | ( | ( | Developed design narrative: --equipment sizing criteria |
| --- | --- | --- | --- |
|  |  |  | Equipment list / design calculations and literature showing capacities of each piece of equipment |
|  |  |  | Control diagram(s) / refrigeration piping schematics indicating: --operation sequence --equipment locations --panel / device placement for refrigerant detectors and alarms (per Seattle Fire Code 606) |
| Plumbing potable and non-potable, acid and laboratory waste, waste and drains, compressed air, vacuum, nitrogen, natural gas, and RO/DI | ( | ( | Developed design narrative: --testing, water treatment, & flushing requirements for all piping systems --equipment, fixture, and outlet selections / catalog information |
|  | ( | ( | Updated calculations (indicate energy balances): --pump head calculations --anticipated flow rates for meter size verification |
|  | ( | ( | Piping plans showing maintenance access considerations: --controllers and headers --isolation valve locations --expansion joints and anchors and glide and roller locations --water service point-of-service connection --waste and drains inverts and point-of-service connections --equipment and fixture layouts --pipe riser / chase locations and horizontal pipe distribution --backflow prevention --for new services: foundation wall invert elevations of all plumbing entering and leaving a building --for RO/DI systems show layout of the series piping distribution loop |
|  |  |  | Preliminary equipment schedules. |
|  |  |  | Legend |
|  |  |  | Proposed details: --pipe headers --coils and conductors --pump installations --seismic anchorage |
|  | ( | ( | One-line systems riser diagrams showing all equipment, meters, coils, fixtures, valves, recirculation lines, and pipe size. |
| Fire Protection | ( | ( | Developed floor plans showing: --valves (dry pipe, sectional, and post indicator valve) --main drains with sanitary sewer connection |
|  |  |  | Proposed details including standpipe and post indicator valves. |
|  | ( | ( | One-line riser diagram: --indicate fire (pump truck) connection |
|  | ( | ( | Edit EH&S “Fire Protection and Standpipes” guide specification customized for Project: --identify special considerations (prescriptive head layouts, head temperature ratings) --specify water supply information |

| HVAC Piping process and environmental chilled water, central cooling water, steam and condensate, and hydronic heating | ( | ( | Developed design narrative and design calculations: --water treatment and flushing program for all piping systems --HVAC piping pressure testing and flushing criteria --equipment selections with catalog information |
| --- | --- | --- | --- |
|  | ( | ( | Developed design calculations (indicate energy balances): --anticipated flow rates for meter size verification |
|  | ( | ( | HVAC piping plans, showing maintenance access requirements: --controllers and headers --isolation valve locations --expansion joints and anchor locations --pipe guide and roller locations --water service point-of-service connection --waste and drains inverts and point-of-service connections --equipment layouts --pipe risers / chase locations and horizontal pipe distribution --for new services, foundation wall invert elevations of all HVAC piping entering and leaving the building |
|  |  |  | Equipment schedules. |
|  |  |  | Legend |
|  |  |  | Proposed details: --pipe headers --coils and conductors --pump installations --seismic anchorage |
|  | ( | ( | One-line systems riser diagrams showing all equipment, meters, coils, valves, and pipe sizes. |
| HVAC | ( | ( | Developed design narrative: --filters, equipment, coils, and diffusers catalog cut sheets --HVAC ductwork pressure testing criteria |
|  | ( | ( | Developed design calculations: --fan curves showing duct rating will withstand deadhead fan pressure of the specified fans --motors and VFD’s harmonic level estimates showing if filtering is req’d |
|  | ( | ( | HVAC duct layout plans with sizing: --quantity and location of motors requiring Variable Frequency Drives --terminal boxes and filters with service access considerations --thermostat locations --diffusers (by types and applications) --fire-smoke and volume dampers --fume hood and biosafety cabinet locations with ducting and fans --cold room(s) ventilation and dehumidifiers (if occupied) --elevator and stair pressurization systems |
|  |  |  | Room pressurization schedule including elevator & stair pressurization. |
|  |  |  | Equipment schedules with sizing. |
|  |  |  | Shafts @ 1/2" scale minimum. |
|  | ( | ( | Mechanical rooms and penthouses equipment layouts @ 1/4" scale min: --identify equipment service access requirements and clearances |
|  | ( | ( | One-line systems flow and riser diagrams. |
|  | ( | ( | Laboratory Computational Fluid Dynamics (CFD) air flow analysis. http://www.ehs.washington.edu/fsodesignrev/1e-rwdi.pdf |
|  | ( | ( | Edit applicable FSDG guide specifications customized for Project: --“Filters used in HVAC Systems” --“Motors and VFDs” |

| Environmental Controls | ( | ( | Developed design narrative: --initial set-points for user adjustable values --sequences of operation for all controlled equipment --HVAC equipment responses to fire and loss of normal power --smoke control and annunciation. |
| --- | --- | --- | --- |
|  | ( | ( | Control diagrams with panel locations. |
|  | ( | ( | Controls points list. |
|  | ( | ( | Edit FSDG “Environmental Control Systems” guide specification customized for Project. |
| Commissioning and TAB | ( | ( | Developed design narrative. |
|  | ( | ( | Edit applicable FSDG guide specifications customized for Project: --Commissioning of HVAC, plumbing, or Electrical systems --Electrical – “Inspection, Calibration, and Testing” --“TAB/Small Projects” or TAB/Large Projects” |
| Audio Visual (AV) | ( | ( | AV systems infrastructure and pathway plan: --conduit sizes, junction boxes, and required pull boxes |
|  | ( | ( | AV systems cable plant one-line diagram showing: --system components, electrical receptacles and communications outlets |
|  |  |  | Equipment interconnection matrix - show cable type and count. |
|  | ( | ( | AV equipment control system panel layout. |
|  |  |  | Equipment rack elevations (in closets, podium, and/or casework). |
|  |  |  | Proposed AV equipment cut sheets. |
| Electrical: Primary Distribution | ( | ( | Developed design narrative: --hardware connection information |
|  | ( | ( | Drawings: --connections to the Campus primary distribution system --distribution routing --conductor and raceway sizing and circuiting |
|  |  |  | Proposed details: --protection and grounding |
|  | ( | ( | Developed one-line diagram. |
| Medium Voltage Switchgear | ( | ( | Developed design narrative: --protection / coordination requirements |
|  | ( | ( | Plan and elevations showing: --equipment location / sizes --front elevations and sectional views / shipping splits |
|  |  |  | Proposed details: --fault bracing and seismic anchors |
|  |  |  | Assembly and wiring diagrams. |
| Load Interrupter Switches | ( | ( | Developed design narrative: --manufacturer and model number --equipment fault duty calculations |
|  | ( | ( | Plan showing: --cable routing and switch lineup / expansion provisions |
|  |  |  | Proposed details: --cable bending radius, termination, and grounding |

| Emergency Power and ATS | ( | ( | Developed design narrative: --CMCS I/O points list |
| --- | --- | --- | --- |
|  | ( | ( | Developed load calculations / schedule: --generator sizing calculations |
|  | ( | ( | Drawings (with source of emergency power): -- equipment infrastructure / locations, layouts and raceway routings |
|  | ( | ( | Developed one-line diagram. |
|  | ( | ( | Edit FSDG "ATS" guide specification customized for Project. |
| Electrical: Building Services | ( | ( | Electrical room plan, elevations, and sectional views @ 1/4” scale min: --equipment / footprints and working clearances, including transformers, switchboards and panelboards (layout for largest equipment) |
|  | ( | ( | Developed one-line diagram showing all equipment. |
| Transformers | ( | ( | Developed design narrative: --manufacturer, model / rating based upon updated load calculations |
|  | ( | ( | Proposed details: --connections, seismic supports, housekeeping pads --secondary containment for liquid-filled transformers |
| Switchboards and Panelboards | ( | ( | Developed fault, load, and seismic calculations. |
|  | ( | ( | One-line wiring diagrams. |
|  | ( | ( | Proposed details: --fault bracing, seismic anchors, shipping splits |
| Monitoring and Metering | ( | ( | Metering and monitoring infrastructure one-line diagram. |
|  | ( | ( | Elevations showing layout of metering equipment in switchboards and other electrical equipment, including MCCs. |
| Motor Control Center (MCCs) and VFDs | ( | ( | Developed design narrative: --VFD harmonic level calculations and filtering requirements |
|  | ( | ( | Plans showing the location of MCCs and motors/VFDs with feeder conduit routing (indicating MCC, motors, conduit, and conductor sizes) and MCC elevations showing the motor and capacitor cubicles. |
| Building Power Distribution and Power Quality | ( | ( | Developed load calculations. |
|  | ( | ( | Electrical rooms / equipment @ 1/4" scale minimum. |
|  | ( | ( | Proposed details of power quality equipment: --seismic and housekeeping pads |
| Electrical: Grounding | ( | ( | One-line riser diagram for grounding systems. |
|  | ( | ( | Proposed details: --grounding buses, lightening terminals, and other grounding equipment |
| Electrical: Raceways | ( | ( | Plans showing exterior duct banks and conduit (show on Site Improvements), cable trays for medium and low voltage systems, Surface Mounted Raceway (SMR), and other required raceway systems with distribution routings. |
| Electrical: Wire, Cable, and Terminations | ( | ( | Cable schedules / sizing. |
|  | ( | ( | Proposed details: --connection hardware, protection methods, and grounding information |
|  | ( | ( | Edit FSDG "MV Wire, Cable and Terminations" guide specification customized for Project. |

| Electrical: Wiring Devices | ( | ( | Plans showing device types, circuiting concepts, locations and heights. |
| --- | --- | --- | --- |
|  | ( | ( | Details for special applications. |
| Electrical: Identification | ( | ( | Edit FSDG “Electrical Identification” guide specification customized for Project. |
| Power System Studies | ( | ( | Preliminary short circuit study. |
|  | ( | ( | Edit FSDG “Power Systems Studies” guide specification customized for Project. |
| Lighting | ( | ( | Light level calculations / factors used in calculating light levels. |
|  | ( | ( | Fixture and lamp selections. |
|  | ( | ( | Lighting and fixtures switching plans: --emergency lighting & exit lighting locations --classroom lighting zone matrix (ref: Classroom Support Services Design Guidelines) |
|  | ( | ( | Site lighting |
| Clock and Bell | ( | ( | Developed riser diagram / location of control panel and point-of-service. |
|  | ( | ( | Plans showing locations of clocks and bells: --bell shutoff switches in classrooms and other learning spaces |
| Miscellaneous Signal Systems | ( | ( | One-line riser diagrams for each system / size calculations. |
|  | ( | ( | Plans showing device locations and raceway routing: --equipment layout (space requirements) |
|  | ( | ( | Proposed wiring interconnection details of systems. |
| Fire Alarm | ( | ( | Plans showing: --main conduit routing --FACP, terminal cabinets, and annunciator locations --auxiliary interface / HVAC, door holders, elevators, and fire sprinklers |
|  | ( | ( | One-line riser diagram / fire alarm zones. |
|  | ( | ( | Strobe design calculations. |
|  | ( | ( | Edit EH&S “Fire Alarm System” guide specification customized for Project |
| CAAMS | ( | ( | Plans with headend backboard location: --show cable routing and location of cable risers |
|  |  |  | Panel layouts |
|  |  |  | CAAMS door schedule and door details. |
| CCTV | ( | ( | Floor plan with locations of cameras and pathway. |

| Communications: Infrastructure Voice & Data / WIFI / CATV / IRS | ( | ( | Plans / UW room numbers: --demo of existing systems / continuity of areas to remain in service plan --MDF & IDF rooms / sleeves indicating quantity and size --cable tray routing and tray size / sleeves indicating quantity and size (coordinate capacity with Classroom Support Services requirements) --vertical and horizontal pathways transitions / details --station conduit pathway and SMR --outlet locations and ID numbers --indicate “building services” pathway requirements for CAAMS, irrigation, DDC, and other monitored building services --IDF service area boundary indicating service distances over 90 meters --CATV box locations --coordinate / Owner’s systems furniture, and Classroom Support Services communication station conduit requirements |
| --- | --- | --- | --- |
|  |  |  | Updated MDF/IDF Analysis Worksheet. |
|  |  |  | Updated Classroom Analysis Functional Use Analysis Worksheet. |
|  |  |  | Outlet schedule in 8 ½” x 11” format with UW room numbers: --include existing and existing to be demolished outlets |
|  |  |  | Edit UW-IT “Infrastructure” guide specification customized for Project: --provide product samples with information for proposed products |
|  | ( | ( | Dimensioned MDF & IDF 1/4” scale plans with “butterfly” wall elevations: --backboards and cable tray in plan and elevation --rack layout plan and elevations (front/back) with ladder tray --indicate HVAC units, plumbing piping, electrical receptacles |
|  | ( | ( | Developed one-line riser diagrams: --include cable plant |
| Communications: Cable Plant Voice & data / WIFI / CATV / IRS | ( | ( | Developed design narrative: --identify rack system power requirements |
|  | ( | ( | All components shown on 1/4" scale “butterfly” wall elevations. |
|  |  |  | Edit UW-IT “Voice, Data, and Multimedia Cable Plant” guide specification customized for Project: --provide product samples with information for proposed products |
|  | ( | ( | CATV riser distribution diagram with cable loss calculations. |
|  |  |  | CATV cable matrix in 8 ½” x 11” format. |
|  | ( | ( | CATV signal loss diagram. |
|  | ( | ( | IRS distribution diagram. |
| End of Attachment B – Design Development Phase Deliverables |

The following Construction Documents deliverables are required for any heading marked for the Schematic Design and Design Development Phases.

| Headings and Items | Construction Documents Phase |
| --- | --- |
| CAD Files | Electronic submittal of all Construction Drawings for Owner’s CAD standards / format review. |
|  | Electronic submittal of all floor plans with room numbers for Owner’s CAD standards / room numbering review. |
| Sustainable Design | Updated CPO “SustainAbilities Scorecard” or for LEED an updated 2 to 4 page summary of the strategies used to achieve LEED credits. |
|  | For state funded LEED projects, the completed Washington State Department of General Administration “Energy and Water Metering Plan” form, and the High – Performance Green Buildings “Post Construction Submittal” form (for energy and water-sewer savings / consumption estimates). |
|  | LEED Project requirements narrative for systems to be commissioned: --owner and user requirements --environmental and sustainability goals --energy efficiency goals --indoor environmental quality requirement --equipment and system expectations --building occupant and O&M personnel requirements |
|  | Provide MSDS for paints, sealants, coatings and other specified materials. |
| Project Manual and Calculations | Edit Owner’s Division 00 documents and 01 Specifications customized for Project and provide Divisions 02 – 49 documents. |
|  | Final list of proprietary bid items by Section. |
|  | List of Project record CAD Shop Drawing submittals required by the Contract Documents, in order by Section. |
|  | Electronic submittal of the final Structural, Mechanical, and Electrical calculations in PDF format identified with the submittal date, A/E name, UW Project name and number and the UW facilities number (FACNUM) with a table of contents by Section/discipline, for all required Construction Documents Phase calculations. |
|  | Electronic submittal of the final basis-of-design narratives in PDF format and identified with the submittal date, A/E name, UW Project name and number and the UW facility number (FACNUM) with at table of contents by Section/discipline. |
| Acoustics | Final calculations showing compliance with design Noise Coefficient (NC) criteria. |
| Temporary Construction Facilities | Temporary construction facilities Drawings and Specifications. |
|  | Detailed phasing plans with mitigations for impacts to adjacent occupied facilities. |
|  | Infection control plans (medical facilities projects). |
| Landscaping and Irrigation | Irrigation design calculations. |
|  | Demolition plan, irrigation plan for new irrigation, and temporary irrigation plan to maintain existing landscape to remain during construction. |
| Refrigeration | Capacity balance curves showing operating balance conditions for matching components. |
| Plumbing and HVAC Piping | Final basis-of-design narrative and calculations: --pump design calculations with data showing pump impeller diameter and curve (for VAV pumps provide data of pumps at maximum and minimum rpm) --identify piping systems “operating pressures” |
|  | For new construction, foundation wall invert elevations of all piping entering and leaving the building. |
| HVAC | Final basis-of-design narrative and calculations: --final equipment / filter selections and cut sheets --calculations for sizing life safety fans --energy analysis calculations |

| Environmental Controls | Control sequences of operation: --set points for user adjustable values --HVAC equipment responses to fire and loss of normal power --smoke control annunciation. |
| --- | --- |
|  | Control point list indicating all input/output requirements. |
|  | Control diagrams including FA/MCC connection. |
| Commissioning and TAB | Final scope of work description for systems and equipment to be commissioned: --primary design assumptions --performance criteria narrative descriptions --design standards put into practice |
|  | Final scope of work description for balancing activities. |
| Audio Visual | AV equipment cut sheets. |
|  | Equipment rack elevations and interconnection matrix. |
| Medium Voltage Switchgear | Coordination study: --incorporate switchgear information in coordination study and specifications |
| Load Interrupter Switches | Final equipment fault duty calculations and ratings. |
| Emergency Power Systems and ATS | Diagrams of generator control, starting procedures, and sequence of operation: --describe ATS sequence of operation for loss of normal power transfer, generator start, fire alarm and elevator control |
|  | Emergency power load schedule. |
|  | CMCS interconnection diagrams, raceway routings and equipment installation details and ATS interface details. |
| Switchboards and Panelboards | Panel schedules showing circuit numbers and load information. |
| MCCs and VFDs | MCC schedules showing load information and circuit numbers. |
|  | Control wiring diagrams with terminal strip information for control functions. |
| Electrical: Wire, Cable, and Terminations | Details: --location of connections and types of terminations for medium voltage systems and major electrical equipment --connection hardware |
| Power System Studies | Final short circuit study. |
| Lighting | Final design calculations. |
|  | Control diagrams. |
| Miscellaneous Signal Systems | Interconnection system diagrams and equipment schedules. |
| Fire Alarm | Wiring plans and connection details: --MCC / HVAC connection, dampers, and fire sprinklers --elevator shunt trip and door holders --terminal cabinets, relays and control equipment --refrigeration and special extinguisher equipment |
|  | FACP elevation |
| Communications: Infrastructure | All applicable standard UW-IT communications drawings. |
| Communications: Cable Plant | All applicable standard UW-IT communications drawings. |
|  | Final voice & data and/or CATV outlet schedule / locations. |

End of Attachment B - Construction Documents Phase Deliverables