## Asset Data Collection Tool
UWB¦CC Asset Data Collection Tool Rev. November 2025
Fixed Asset # | Asset Tag | Asset Description | Parent | Class | Building | Room # | Location | Manufacturer | Model | Serial Number | Status | Warranty End Date | Install Date | Uniformat | Useful Life | Replacement Cost

## Class
CLASS | CLASS DESCRIPTION | UNIFORMAT CODE
SITE | Campus location
ZONE | Area of campus
BUILDING | State-owned or leased facility
ROOM | Interior building space or area
ELEVATORSYSTEMS | Elevators and elevator-related systems | D1010
ELEVATORALARMS | Elevator emergency phones and alarm systems | D1010
GENERALCONVEYANCES | Dumbwaiters and other simple lifts | D1090
SPECIALASSISTCONVEYANCE | Stairwell chair lifts, interior wheelchair lifts, other | D1090
GENERALPLUMBINGFIXTURES | General end-use plumbing fixtures | D2010
BATHROOMWASTEFIXTURES | Toilets, urinals, bidets, other | D2010
INSTITUTIONALSINKS | Sinks in bathrooms, breakrooms, other non-program spaces | D2010
PROGRAMSINKS | Classroom, lab, & arts studio sinks and wash stations | D2010
BATHINGFIXTURES | Bathtubs and showers, general use | D2010
EMERGENCYWASH | Emergency showers and eyewash stations | D2010
DRINKINGFOUNTAINS | Drinking fountains, bottle fill station systems | D2010
DOMESTICWATERINTERIORDISTRIBUTION | General building water system elements | D2020
DOMESTICWATERCONDITIONING | Conditioning, treatment systems for domestic water | D2020
HOTWATERHEATERS | Domestic hot water heaters and boilers | D2020
INWALLPLUMBING | Building domestic water plumbing | D2020
DHWSTORAGETANKS | Hot water storage tanks | D2020
DHWEXPANSIONTANKS | Hot water expansion tanks | D2020
DOMESTICWATERPUMPS | Domestic water circulation pumps | D2020
DOMESTICWATERVALVES | Domestic water valves | D2020
WATERBACKFLOWPREVENTERS | Water system backflow preventers | D2020
DHWRECIRCSYSTEMS | Hot water recirculation system components | D2020
DHWSPECIALTY | Heat exchangers, controls, other system components | D2020
SANITARYWASTEDRAINSPIPING | Drain covers, piping, and vents | D2030
BUILDINGDRAINWASTETRAPS | Sediment, grease, & other traps (kitchens, labs, shops, etc) | D2030
RAINWATERPIPING | Discharge piping after roof gutters/drains, either interior or building exterior | D2040
SUMPPUMPS | Internal building sump pumps | D2040
POOLFACILITYSYSTEMS | Swimming pool equipment - filters, treatment, circulation | D2090
DECORATIVEFOUNTAINSYSTEMS | Indoor fountain system components | D2090
AIRSEPARATORS | Air separators for any water systems | D2090
GENERALPLUMBINGCOMPONENTS | Generic, special, or uncategorized plumbing components | D2090
HVACLIQUIDFUELSYSTEMS | Heating oil or other liquid fuel supply system components | D3010
HVACGASFUELSYSTEMS | Propane or natural gas fuel supply system components - incl. utility meters | D3010
HVACTHERMALSUPPLYSYSTEMS | Campus thermal loop system components outside the buildings - incl. utility meters | D3010
HVACBUILDINGENERGYMETERS | Building-level gas, electric, or other fuel or energy meters | D3010
STEAMBOILERS | Boilers, any fuel, creating steam, plus supporting components | D3020
HEATINGHOTWATERBOILERS | Boilers, any fuel, creating hot water for heating plus supporting components | D3020
FURNACES | Furnaces, any fuel, creating hot air, plus supporting components | D3020
HEATINGHEATPUMP | Heating-only heat pumps | D3020
STEAMDISTRIBUTIONSYSTEMS | Steam pipes, traps, pumps, valves, condensate return, makeup water, etc | D3020
HEATINGHWDISTRIBUTIONSYSTEMS | Heating hot water pipes, pumps, valves, air separators, motors, etc | D3020
HEATRECOVERY | Heat recovery wheels, counter-current exchange systems | D3020
UNIQUEHEAT | Other heating systems, plus portable space heaters | D3020
CHILLERS | Cooling chiller | D3030
COOLINGHEATPUMP | Heat pump providing cooling only | D3030
COOLINGTOWEREVAPCOOLERS | Cooling towers and evaporative coolers | D3030
CONDENSINGUNIT | Condensing units on cooling systems | D3030
COOLINGCOMPRESSOR | Compressors on cooling systems | D3030
PACKAGEDAIRCONDITIONING | Packaged and small unit air conditioning systems | D3030
COOLINGFLUIDDISTRIBUTION | Piping, pumps, valves, components for cooling fluid distribution | D3030
SPLITAIRCOND | Split system air conditioners | D3030
UNIQUECOOLING | Chilled beams, swamp coolers, portable, and other cooling systems | D3030
AIRCIRCCOMPONENTS | Supply and exhaust ductwork, grills, dampers, actuators, sensors, etc | D3040
MAKEUPAIR | Make-up air units and system components | D3040
DISTRIBUTIONFANS | Air distribution fans | D3040
PRESSURIZATIONFANS | Pressurization fans | D3040
EXHAUSTFANS | General exhaust fans | D3040
SPECIALTYEXHAUSTS | Kitchen, lab hood, studio, and shop ventilation and exhaust systems | D3040
CEILINGFANS | Ceiling and other in-room circulation fans | D3040
HVACGENERALCOMPONENTS | HVAC motors, pumps, fans, valves, etc. not directly associated with primary generation systems | D3040
PACKAGEDHVAC | Mixed heating and cooling units | D3050
PACKAGEDAIRHANDLERS | Air handling units | D3050
HEATCOOLHEATPUMPS | Heat pump systems providing both heating and cooling | D3050
HEATPUMPHEATEXCHANGERS | Both source and distribution side heat pump exchangers and circulation systems | D3050
REFRIGERANTCONTAININGUNIT | Discrete compression, expansion, piping system containing refrigerant, per Dept of Ecology Refrigerant Management Program | D3050
TERMINALHEATING&COOLINGUNIT | Terminal units providing both heating and cooling - systems and components | D3050
TERMINALVENTILATORUNITS | Terminal ventilation-only unit systems and components | D3050
TERMINALHEATINGUNITS | Terminal heating-only unit systems and components | D3050
TERMINALCOOLINGUNITS | Terminal cooling-only unit systems and components | D3050
RADIANTHEATERS | In-room radiant heat systems | D3050
FANCOILUNITS | Fan coil units and components | D3050
VARIABLEAIRVOLUME | VAV units and components | D3050
VARIABLEREFRIGFLOW | Variable Refrigerant Flow systems and all unique components | D3050
BUILDINGAUTOMATIONCONTROLS | Automated control systems and supporting components - sensors, software, etc | D3060
SYSTEMLEVELCONTROLS | Boiler, chiller, air handler, and other system-level controls | D3060
ENERGYMONITORINGMANAGEMENT | Energy management tools, monitoring software, and supporting components | D3060
CONTROLDATAHARDWARE | Data cabling, switches, processors, and other supporting hardware | D3060
HVACTESTINGBALANCING | Equipment, tools specific for systems balancing | D3060
HUMIDITYCONTROL | General humidity control systems | D3090
AIRDRYERS | Air drying systems | D3090
AIRFILTRATION | Special air filters, purifiers, and dust collection | D3090
AIRCURTAIN | Air curtain systems and components | D3090
AIRQUALSENSORS | Air quality sensors - CO, CO2, radon, gas, other | D3090
REFRIGERANTLEAKDETECTION | Automated refrigerant leak detection systems | D3090
FIRESPRINKLERSYSTEMS | Wet and dry fire sprinklers and immediate connections | D4010
FIRESTANDPIPES | Standpipes and water supply system equipment | D4020
FIRESYSTEMVALVES | Sprinkler system valves and test points | D4020
FIREPUMPS | Sprinkler system pumping equipment | D4020
FIREEXTINGUISHERS | Fire Extinguishers, mounts, cabinets | D4030
FIREHOSES | Fire hoses, cabinets | D4030
FIRESAFETY | Other fire safety equipment, containment, doors, egress systems | D4030
FIREDETECTION | Smoke sensors, pull stations, other alarms | D4090
FIREPANELS | Fire system panels and associated communication lines/systems | D4090
FIREANNUNCIATORS | Fire alarm lights and horns | D4090
ELECTRICSERVICECONNECTIONS | Overhead and buried service connections | D5010
ELECTRICALPANELSBREAKERS | Distribution switch gear, panels, and breakers | D5010
TRANSFORMERS | Building service transformers | D5010
RENEWABLEENERGY | Solar PV or other renewable energy systems, all components | D5010
ELECTRICALUTILITY | Utility electrical meter | D5010
INTERIORLIGHTING | Interior lighting fixtures and service wiring | D5020
EXTERIORBUILDINGLIGHTING | Exterior lighting fixtures and service wiring | D5020
EXITLIGHTING | Exit lighting fixtures | D5020
LIGHTINGCONTROLS | Lighting controls, switches, sensors | D5020
OPENFACILITYLIGHTING | Open facility and sports field lighting systems and controls | D5020
BUILDINGPUBLICADDRESS AND ALARMS | Building-level public address and alarm annunciators | D5030
BUILDINGINTERCOMMUNICATIONPAGING | Building intercommunication and paging system specific components | D5030
BUILDINGTELEPHONE | Building-level telephone system components | D5030
CLOCKS | Clocks, programming, and connectivity systems | D5030
DISPLAYS | Visual monitor display and announcement systems | D5030
BUILDINGSECURITY | CCTV, call boxes/phones, panic buttons, other security detection and response system components | D5030
ACCESSCONTROLS | Electronic access control sensor and lock networks and controls, automated lockdown systems | D5030
COMMUNICATIONNETWORK | Building-mounted communications towers, antennae, other network infrastructure | D5030
DATACOMMUNICATIONS | Data communications system elements | D5030
EMERGENCYLIGHTING | Emergency lighting systems, excluding exit signage | D5090
EMERGENCYPOWER | Uninterruptible power supply, inverters, disconnects, other emergency power and control systems | D5090
EMERGENCYGENERATOR | Emergency generator and fuel supply | D5090
FAULTPROTECTION | Ground-fault, lightning, other | D5090
POWERCORRECTION | Power factor correction systems | D5090
SHOREPOWER | Exterior power hookup for mobile service, lab, other vehicles | D5090
PROGRAMKITCHENCULINARY | Kitchen stoves, ovens, coolers and other culinary arts program fixtures and equipment | E1010
PROGRAMMEDICALVET | Medical, nursing, EMT, veternary program fixtures and equipment | E1010
PROGRAMAUTOMOTIVEINDUSTRIAL | Automotive hoists and lifts, welding booths, cranes, and other industrial program fixtures and equipment | E1010
PROGRAMAGRICULTURAL | Agricultural program fixtures and equipment | E1010
PROGRAMSCIENCES | Science program and lab fixtures and equipment | E1010
PROGRAMARTS | Arts program kilns, forges, brazing hoods, other fixtures and equipment | E1010
PROGRAMOTHER | Misc. built-in or long-term program support fixtures and equipment | E1010
PROGRAMATHLETICS | Athletic program equipment and fixtures | E1010
PROGRAMDATAIT | Data Services, IT program equipment and associated systems (not general building service) | E1010
INSTITUTIONALEMERGENCYRESPONSE | AED devices and cabinets, first aid, emergency response fixtures and equipment | E1020
INSTITUTIONALAIRCOMPRESSION | Air compression systems and associated components - compressors, dryers, motors, hoses, etc | E1020
INSTITUTIONALVACUUMSYS | Non-program vacuum generation and pneumatic systems | E1020
INSTITUTIONALFOODSVC | Prep, kitchen, and service fixtures and equipment for public food service | E1020
PORTABLECUSTODIAL | Custodial equipment | E1020
PORTABLEGROUNDSMAINT | Grounds and maintenance non-vehicular equipment | E1020
PORTABLESECURITYSAFETY | Security, health and safety equipment | E1020
INSTITUTIONALLAUNDRY | Washers, dryers, laundry facility fixtures and equipment | E1020
SANITATIONFIXTURES | Soap/sanitizer dispensers, paper towels, hand air dryers, other | E1020
INSTITUTIONALOTHERSERVICE | Ice, vending machines, other special service provision fixtures | E1020
INSTITUTIONALHAZMAT | Hazardous material handling and storage fixtures and equipment | E1020
INSTITUTIONALART | Indoor art installations and associated lighting, plumbing, or other fixtures | E1020
VEHICLESROAD | Road-legal, licensed vehicles and accessories | E1030
VEHICLESNONROAD | Non-road vehicles and accessories - including boom, fork, and other mobile lifts | E1030
PARKINGCONTROL | Parking pay stations, gates, other fixtures or equipment | E1030
LOADINGDOCK | Loading dock lifts, leveling assemblies | E1030
NONPROGRAMHOISTSLIFTS | Maintenance, fleet, and shops stationary hoists and lifts | E1030
EVCHARGING | Electric vehicle charging stations and associated equipment | E1030
FUELINGSTATIONS | Institutional vehicle fueling stations | E1030
SOLIDWASTE | Bins, compactors, other solid waste collection and handling fixtures and equipment | E1090
RESIDENTIAL | Student housing appliances and fixtures | E1090
OTHERPURPOSEEQUIPMENT | Stuff that doesn't fit elsewhere | E1090
FIXEDINTERIORFURNISHINGS | Built in furnishings | E2010
MOVABLEINTERIORFURNISHINGS | Movable interior furnishings | E2020
EXTERIORBUILDINGFURNISHINGS | Any exterior furnishings specifically associated with a single building | E2030
TEMPORARYSTRUCTURES | Tents, canopies, other temporary structures or structural extensions | F1000
OTHERSPECIALSTRUCTURES | Non-classifiable special purpose structures or constructions, both institutional and programmatic (such as cooling towers) | F1000
VAULTS | Utility vaults | F1000
STORAGETANKS | Underground and aboveground fuel storage tanks | F1000
MONITORINGWELLS | Underground storage tank monitoring wells and equipment | F1000
ROADINFRASTRUCTURE | Campus roads, curbs, barriers, drainage, etc. | G2010
VEHICULARBRIDGES | Campus vehicle-rated bridges | G2010
PARKINGLOTPAVING | Campus parking lot paving and curb infrastructure | G2020
OTHERPARKING | Parking-related infrastructure and/or systems | G2020
PAVEDWALKWAYS | Pedestrian sidewalks and campus walkways, including ADA infrastructure | G2030
PEDESTRIANBRIDGES | Pedestrian bridge structures | G2030
CAMPUS/WAYFINDINGSIGNAGE | Entry and directional signage | G2030
FENCESGATES | Campus fences and gates | G2040
RETAININGWALLS | Campus retaining walls and associated drainage | G2040
OUTDOORART | Campus statuary and other art installations | G2040
GENERALRECREATIONAL | Campus athletic and play field site development and supporting fixtures | G2040
WATERWORKS | Campus fountains, ponds, and waterways | G2040
LANDSCAPEDGROUNDS | Campus landscaped areas | G2050
SPECIALGARDENS | Campus ornamental, herbal, other special purpose gardens or conservation areas | G2050
SPECIALTREES | Campus trees designated for protection or other care | G2050
GROUNDSIRRIGATION | Campus irrigation systems and components | G2050
POTABLEWATER | Potable water supply infrastructure and system elements outside of buildings | G3010
WATERWELLS | Campus water wells and associated pumps, filters, and other equipment | G3010
FIREPROTECTIONINFRASTRUCTURE | Campus fire loop pumps, piping, hydrants, and other associated equipment | G3010
WATERTREATMENT | Campus fresh water treatment systems | G3010
WATERMETERS | Utility and campus consumption and deduct meters | G3010
SEPTICSYSTEM | Septic tanks, drainfields, and associated equipment | G3020
SEWERSYSTEM | Utility sewer pipes, manholes, lift stations, and associated infrastructure | G3020
STORMSEWER | Campus rainwater drainage and piping | G3030
PARKINGLOTSTORMDRAIN | Campus parking lot stormwater drainage and oil seperator systems | G3030
SURFACERAINWATERINFRA | Campus rain gardens, headwalls, bioswales, catch basins, retention ponds, and other surface rainwater management | G3030
PRIMARYELECTRICAL | Primary electrical feed meter, transformer, switch, and other associated equipment | G4010
PRIMARYDISTRIBUTION | Campus primary distribution lines and associated equipment outside of buildings | G4010
LIGHTPOLES | Light poles and standards | G4020
OUTDOORLIGHTING | Campus exterior road, path, and grounds lighting fixtures and components | G4020
CALLBOXES | Emergency call boxes, phones, other communication access outside of buildings | G4030
PUBLICADDRESS | Exterior campus announcement and alarm systems | G4030
DATAINFRASTRUCTURE | Exterior campus data cabling, broadcast, other system components | G4030
SITECOMMUNICATIONSOTHER | Campus telephone, radio, other communications system network components | G4030
CAMPUSCATHODIC | Electrical cathodic protection system components | G4090
CAMPUSTUNNELS | Service and utility tunnels | G9010
OTHERSITEDEVELOPMENT | General, uncategorized campus site systems or components | G9090

## Buildings & Rooms
BUILDING | BUILDING CODE | ARC | CHAS | CP1 | DISC | TRUL | LB1 | LB2 | LBA | UW1 | UW2 | PHW | SSGC | SPKG | NPKG | WPKG | HH
Activities & Recreation Center | ARC | 000A | 100B | 001A | 010P | 100 | EL1 | 001A | 000A | 000A | 001A | 100 | 101 | 1ST1 | 1ST2 | 1ST1 | 1000A
Chase House | CHAS | 000B | 100 | 001B | 010Q | 100A | EL2 | 001B | 000B | 000B | 001B | 101 | 102 | 1ST2 | 1ST1 | 1ST2 | 1000B
Cascadia Building 1 | CC1 | 000C | 101C | 001C | 010R | 101 | 1ST1 | 001C | 000C | 000C | 001C | 102 | 103 | 2ST1 | 2ST2 | 2ST1 | 1000C
Cascadia Building 2 | CC2 | 000D | 1ST1 | 001D | 010S | 101A | 1ST2 | 001D | 001A | 000D | 001D | 103 | 104 | 2ST2 | 2ST1 | 2ST2 | 1000D
Cascadia Building 3 | CC3 | 000E | 2ST1 | 001E | 010T | 102 | 1ST3 | 001E | 001B | 000E | 001E | 104 | 105 | 3ST1 | 3ST2 | 3ST1 | 1000E
Physical Plant | CP1 | 000F | 202A | 001F | 050 | 104 | 2ST1 | 001F | 001C | 000G | 001F | 105 | 106 | 3ST2 | 3ST1 | 3ST2 | 1000F
Discovery Hall | DISC | 000G | 100A | 001G | 051 | 105 | 2ST2 | 010G | 001D | 001A | 001G | 106 | 107 | 4ST1 | 4ST2 | 4ST1 | 1000G
Truly House | TRUL | 001 | 201 | 100A | 052 | 105A | 2ST3 | 001H | 001E | 001B | 001H | 201 | 108 | 4ST2 | 4ST1 | 4ST2 | 1001A
Campus Library | LB1 | 002 | 202 | 101A | 053 | 105B | 100A | 001J | 001F | 001C | 001J | 1ST1 | 109 | 5ST1 | 101 | GST1 | 1001B
Library Building 2 | LB2 | 003 | 106 | 101B | 054 | 106 | 100B | 001K | 002 | 001D | 001K | 1ST2 | 100 | 5ST2 | 1EL1 | 1EL1 | 1001C
Library Annex | LBA | 004 | 101 | 101C | 061 | 106A | 100C | 001L | 003 | 001E | 001L |  |  | 101 | 2EL1 | 2EL1 | 1001D
Founders Hall | UW1 | 005 | 101A | 101D | 061A | 107 | 101A | 002 | 004 | 001F | 002 |  |  | 1EL1 | 3EL1 | 3EL1 | 1001E
Commons Hall | UW2 | 008 | 102 | 102 | 062 | 107C | 101B | 003 | 005 | 001G | 004 |  |  | 2EL1 | 4EL1 | 4EL1 | 1001F
Physical Plant Warehouse | PHW | 009 | 105 | 104 | 063 | 201 | 101C | 003A | 005A | 001H | 005 |  |  | 3EL1 | 102 | 100A | 1001G
Sarah Simonds Green Conservatory | SSGC | 010 | 104 | 105 | 064 | 201A | 101D | 003B | 005B | 005 | 006 |  |  | 4EL1 | 103 | 100B | 1001H
South Parking Garage | SPKG | 015 | 104A | 106 | 066 | 201B | 101E | 003C | 005D | 007 | 010J |  |  | 5EL1 | 203 | 100C | 1001J
North Parking Garage | NPKG | 016 |  | 107 | 0ST1 | 202 | 101F | 005 | 0ST1 | 007A | 010L |  |  | 105 | 204 | 101 | 1001K
West Parking Garage | WPKG | 017 |  | 108 | 0ST3 | 202A | 101G | 005A | 100A | 007B | 011 |  |  | 106 | 301 | 103 | 1001L
Husky Hall | HH | 018 |  | 109 | 100P | 203 | 102 | 006 | 100B | 010 | 020 |  |  | 202 | 302 | 105 | 1001M
Innovation Hall | INV | 019 |  | 110 | 100Q | 203A | 105 | 1ST2 | 101A | 011 | 021 |  |  | 203 | 401 | 200A | 1001N
Campus Zone | CMPZ | 020 |  | 110A | 100R | 204 | 107 | 010 | 102 | 020 | 026 |  |  | 301 | 402 | 200B | 1001P
Sports Field Zone | SFZ | 021 |  | 110B | 100T | 204A | 108 | 010D | 102A | 021 | 030 |  |  | 302 | 201 | 200C | 1001Q
Surface Lots Zone | SLZ | 022 |  | 111 | 100U | 1ST1 | 110 | 010A | 102B | 030 | 030A |  |  | 401 | 202 | 207 | 1110
Wetlands Zone | WLZ | 030 |  | 112 | 100V | 2ST1 | 111 | 010B | 102C | 031 | 030B |  |  | 402 |  | 300A | 1120
New Build | NEW | 030A |  | 113 | 150 | 200 | 114 | 010C | 102D | 040 | 030C |  |  | THMP501 |  | 300B | 1130
|  | 040 |  | 100 | 151 |  | 118 | 020 | 102E | 041 | 031 |  |  | THMP502 |  | 300C | 1130A
|  | 040A |  | 110C | 152 |  | 120 | 030 | 102F | 044 | 036 |  |  | 102 |  | 400A | 1140
|  | 0ST2 |  | 101CA | 153 |  | 122 | 0EL1 | 102G | 045 | 040 |  |  | 103 |  | 400B | 1150
|  | 100A |  | 101DA | 155 |  | 122A | 0EL2 | 103 | 050 | 041 |  |  | 104 |  | G00A | 1160
|  | 100B |  |  | 161 |  | 122B | 0EL3 | 104 | 051 | 0EL1 |  |  | 201 |  |  | 1160A
|  | 100C |  |  | 162 |  | 122C | 0ST1 | 105 | 060 | 0ST1 | [5 empty] | 1160B
|  | 100D |  |  | 165 |  | 1EL1 | 101A | 105A | 061 | 0ST2 | [5 empty] | 1160C
|  | 100E |  |  | 165A |  | 1EL2 | 101B | 105B | 061A | 100J | [5 empty] | 1209
|  | 100F |  |  | 165B |  | 200A | 101C | 105C | 061B | 100K | [5 empty] | 1210
|  | 100G |  |  | 167 |  | 200B | 101D | 106 | 070 | 100L | [5 empty] | 1210A
|  | 100H |  |  | 169 |  | 200C | 101K | 107 | 070A | 100N | [5 empty] | 1211
|  | 110 |  |  | 1ST1 |  | 200D | 102 | 108 | 070B | 101B | [5 empty] | 1211A
|  | 115 |  |  | 1ST3 |  | 200E | 103 | 1EL1 | 070C | 101C | [5 empty] | 1212
|  | 116 |  |  | 1ST4 |  | 201A | 104 | 1ST1 | 070D | 101D | [5 empty] | 1215
|  | 117 |  |  | 200P |  | 201B | 105 | 200A | 071A | 101E | [5 empty] | 1216
|  | 118 |  |  | 200Q |  | 201C | 108 | 200B | 080 | 101F | [5 empty] | 1216A
|  | 120 |  |  | 200S |  | 201G | 1EL1 | 201A | 080A | 104 | [5 empty] | 1217
|  | 121 |  |  | 200V |  | 202 | 1EL2 | 202 | 080B | 105 | [5 empty] | 1218
|  | 130 |  |  | 200W |  | 203 | 1EL3 | 203 | 080C | 106A | [5 empty] | 1218A
|  | 130A |  |  | 251 |  | 205 | 1ST1 | 204 | 080D | 106B | [5 empty] | 1221
|  | 130B |  |  | 252 |  | 206 | 200A | 204A | 080E | 106C | [5 empty] | 1221A
|  | 131A |  |  | 253 |  | 207 | 201A | 204AST | 080F | 121 | [5 empty] | 1222
|  | 131B |  |  | 255 |  | 208 | 201B | 204B | 081 | 124 | [5 empty] | 1223
|  | 135 |  |  | 256 |  | 210 | 201C | 204C | 090 | 124A | [5 empty] | 1223A
|  | 140 |  |  | 257 |  | 210A | 201D | 204D | 0EL1 | 124B | [5 empty] | 1224
|  | 141A |  |  | 257A |  | 210B | 202 | 204E | 0ST1 | 124C | [5 empty] | 1227
|  | 141B |  |  | 257B |  | 210C | 203 | 204F | 0ST2 | 124D | [5 empty] | 1228
|  | 142 |  |  | 258 |  | 210D | 204 | 205 | 0ST3 | 130 | [5 empty] | 1228A
|  | 144 |  |  | 260 |  | 210E | 205 | 206 | 100A | 131 | [5 empty] | 1229
|  | 1ST2 |  |  | 261 |  | 210F | 208 | 207 | 100B | 134 | [5 empty] | 1229A
|  | 200A |  |  | 262 |  | 210G | 208A | 208 | 100D | 134A | [5 empty] | 1230
|  | 200B |  |  | 262A |  | 211 | 208B | 209 | 100E | 134B | [5 empty] | 1230A
|  | 200E |  |  | 263 |  | 211A | 208C | 2EL1 | 100F | 134C | [5 empty] | 1232
|  | 200F |  |  | 264 |  | 212 | 212 | 2ST1 | 100G | 134D | [5 empty] | 1232A
|  | 201 |  |  | 265 |  | 213 | 212A | 300A | 100H | 140 | [5 empty] | 1310
|  | 201A |  |  | 267 |  | 213A | 214 | 300B | 100J | 141 | [5 empty] | 1310A
|  | 201B |  |  | 269 |  | 214 | 214A | 301A | 101A | 1EL1 | [5 empty] | 1310B
|  | 201C |  |  | 270 |  | 215 | 216 | 302 | 101B | 1ST1 | [5 empty] | 1311
|  | 202 |  |  | 271 |  | 218 | 218 | 303 | 101C | 1ST2 | [5 empty] | 1312
|  | 210 |  |  | 273 |  | 220 | 218A | 304 | 101D | 200J | [5 empty] | 1312A
|  | 216 |  |  | 2ST4 |  | 221 | 218B | 305 | 101E | 200K | [5 empty] | 1313
|  | 217 |  |  | 2ST5 |  | 222 | 218C | 306 | 101F | 200L | [5 empty] | 1313A
|  | 218 |  |  | 300P |  | 2EL1 | 2ST1 | 307 | 102 | 201B | [5 empty] | 1316
|  | 215 |  |  | 300Q |  | 2EL2 | 300A | 308 | 103 | 201C | [5 empty] | 1317
|  | 235 |  |  | 300R |  | 300A | 300C | 309 | 109 | 201D | [5 empty] | 1318
|  | 240 |  |  | 300S |  | 300B | 300D | 3EL1 | 110 | 201E | [5 empty] | 1318A
|  | 2ST2 |  |  | 300U |  | 300F | 301A | 3ST1 | 111 | 201F | [5 empty] | 1319
|  | ROOF1 |  |  | 300V |  | 301B | 301B |  | 113 | 204 | [5 empty] | 1319A
|  | ROOF2 |  |  | 300X |  | 301C | 302 |  | 115 | 205 | [5 empty] | 1322
|  | 1EL1 |  |  | 351 |  | 301G | 303 |  | 117 | 206 | [5 empty] | 1323
|  | 2EL1 |  |  | 352 |  | 301H | 304 |  | 119 | 208 | [5 empty] | 1411
|  | 0EL1 |  |  | 352C |  | 302 | 305 |  | 120 | 210 | [5 empty] | 1411A
[5 empty] | 352A |  | 303 | 306 |  | 121 | 211 | [5 empty] | 1412
[5 empty] | 352B |  | 305 | 307 |  | 126 | 212 | [5 empty] | 1415
[5 empty] | 352D |  | 308 | 308 |  | 128 | 214 | [5 empty] | 1416
[5 empty] | 352E |  | 310 | 309 |  | 130 | 216 | [5 empty] | 1416A
[5 empty] | 352F |  | 310A | 310 |  | 131 | 218 | [5 empty] | 1418
[5 empty] | 352G |  | 310B | 312 |  | 132 | 220 | [5 empty] | 1419
[5 empty] | 352H |  | 310C | 314 |  | 133 | 221 | [5 empty] | 1420
[5 empty] | 352J |  | 310D | 316 |  | 134 | 222 | [5 empty] | 1420A
[5 empty] | 352K |  | 310E | 318 |  | 135 | 224 | [5 empty] | 1424
[5 empty] | 352L |  | 310F | 3ST1 |  | 136 | 226 | [5 empty] | 1426
[5 empty] | 352M |  | 310G | 3STM3 |  | 137 | 228 | [5 empty] | 1430
[5 empty] | 352N |  | 310H | 0ST2 |  | 138 | 230 | [5 empty] | 1430A
[5 empty] | 352R |  | 311 | 007 |  | 139 | 231 | [5 empty] | 1431
[5 empty] | 352S |  | 311A | 400 |  | 140 | 231A | [5 empty] | 1432
[5 empty] | 352T |  | 311B | ROOF |  | 141 | 235 | [5 empty] | 1433
[5 empty] | 352U |  | 314 | BRIDGE |  | 142 | 240 | [5 empty] | 1433A
[5 empty] | 352V |  | 318 | 106 |  | 143 | 241 | [5 empty] | 1436
[5 empty] | 353 |  | 320 | 4STM3 |  | 144 | 241A | [5 empty] | 1436A
[5 empty] | 355 |  | 321 | 010F |  | 145 | 2EL1 | [5 empty] | 1437
[5 empty] | 357 |  | 322 | 002A |  | 146 | 2ST1 | [5 empty] | 1438
[5 empty] | 357A |  | 323 | 101 |  | 147 | 2ST2 | [5 empty] | 1438A
[5 empty] | 357B |  | 324 | 109 |  | 148 | 300J | [5 empty] | 1439
[5 empty] | 358 |  | 325 | 001G |  | 149 | 300K | [5 empty] | 1442
[5 empty] | 360 |  | 3EL1 | 010H |  | 151 | 300L | [5 empty] | 1443
[5 empty] | 362 |  | 3EL2 | 101E |  | 153 | 300M | [5 empty] | 1443A
[5 empty] | 363 |  | 3ST1 | 107 |  | 155 | 300N | [5 empty] | 1444
[5 empty] | 363A |  | 3ST2 |  |  | 160 | 301B | [5 empty] | 1444A
[5 empty] | 364 |  | 3ST3 |  |  | 161 | 301C | [5 empty] | 1445
[5 empty] | 364A |  | 3ST4 |  |  | 165 | 301D | [5 empty] | 1445A
[5 empty] | 367 |  | ROOF |  |  | 167 | 301E | [5 empty] | 1448
[5 empty] | 367A |  | 200F |  |  | 169 | 301F | [5 empty] | 1449
[5 empty] | 368 |  | 300C |  |  | 170 | 301G | [5 empty] | 1450
[5 empty] | 369 |  | 400 |  |  | 171 | 304 | [5 empty] | 1450A
[5 empty] | 380 |  | 4ST4 |  |  | 172 | 305 | [5 empty] | 1451
[5 empty] | 380A |  | 106 |  |  | 173 | 306 | [5 empty] | 1453
[5 empty] | 381 |  | 4EL2 |  |  | 174 | 307 | [5 empty] | 1454
[5 empty] | 3ST1 |  | 200G |  |  | 175 | 308 | [5 empty] | 1456
[5 empty] | 3ST2 |  | 300D |  |  | 176 | 309 | [5 empty] | 1456A
[5 empty] | 3ST5 |  | 301A |  |  | 177 | 310 | [5 empty] | 1510
[5 empty] | 3ST6 |  | 301J |  |  | 178 | 311 | [5 empty] | 1511
[5 empty] | 400P |  |  |  |  | 179 | 312 | [5 empty] | 1511A
[5 empty] | 400Q |  |  |  |  | 180 | 313 | [5 empty] | 1515
[5 empty] | 400R |  |  |  |  | 181 | 314 | [5 empty] | 1519
[5 empty] | 400S |  |  |  |  | 182 | 315 | [5 empty] | 1520A
[5 empty] | 400U |  |  |  |  | 183 | 316
[5 empty] | 400V |  |  |  |  | 184 | 317
[5 empty] | 451 |  |  |  |  | 185 | 318
[5 empty] | 452 |  |  |  |  | 186 | 319
[5 empty] | 452A |  |  |  |  | 190 | 320
[5 empty] | 452B |  |  |  |  | 191A | 321
[5 empty] | 452C |  |  |  |  | 191B | 322
[5 empty] | 452D |  |  |  |  | 192 | 323
[5 empty] | 452E |  |  |  |  | 194 | 324
[5 empty] | 452F |  |  |  |  | 1EL1 | 325
[5 empty] | 452G |  |  |  |  | 1ST1 | 326
[5 empty] | 452H |  |  |  |  | 1ST2 | 327
[5 empty] | 452J |  |  |  |  | 200A | 328
[5 empty] | 452K |  |  |  |  | 200B | 329
[5 empty] | 452L |  |  |  |  | 200C | 330
[5 empty] | 452M |  |  |  |  | 200E | 331
[5 empty] | 452N |  |  |  |  | 200G | 332
[5 empty] | 452T |  |  |  |  | 201A | 333
[5 empty] | 452U |  |  |  |  | 201B | 334
[5 empty] | 453 |  |  |  |  | 201C | 335
[5 empty] | 455 |  |  |  |  | 201D | 336
[5 empty] | 457 |  |  |  |  | 201E | 337
[5 empty] | 457A |  |  |  |  | 201F | 339
[5 empty] | 457B |  |  |  |  | 202 | 340
[5 empty] | 458 |  |  |  |  | 210 | 341
[5 empty] | 460 |  |  |  |  | 211 | 343
[5 empty] | 461 |  |  |  |  | 211A | 345
[5 empty] | 462 |  |  |  |  | 211B | 347
[5 empty] | 463 |  |  |  |  | 211C | 3EL1
[5 empty] | 463A |  |  |  |  | 211D | 3ST1
[5 empty] | 464 |  |  |  |  | 211E | 3ST2
[5 empty] | 464A |  |  |  |  | 220 | MEL1
[5 empty] | 467 |  |  |  |  | 221 | MEZZ-001K
[5 empty] | 468 |  |  |  |  | 226 | MEZZ-001L
[5 empty] | 469 |  |  |  |  | 228 | MST1
[5 empty] | 469A |  |  |  |  | 230 | 400
[5 empty] | 472 |  |  |  |  | 231 | ROOF
[5 empty] | 474 |  |  |  |  | 232 | 010M
[5 empty] | 476 |  |  |  |  | 233 | 4EL1
[5 empty] | 480 |  |  |  |  | 234 | 4ST2
[5 empty] | 4ST1 |  |  |  |  | 235 | 402
[5 empty] | 4ST2 |  |  |  |  | 236 | 010K
[5 empty] | 4ST6 |  |  |  |  | 237
[5 empty] | 550 |  |  |  |  | 238
[5 empty] | 1EL1 |  |  |  |  | 239
[5 empty] | 1EL2 |  |  |  |  | 240
[5 empty] | 2EL1 |  |  |  |  | 241
[5 empty] | 2EL2 |  |  |  |  | 242
[5 empty] | 3EL1 |  |  |  |  | 243
[5 empty] | 3EL2 |  |  |  |  | 244
[5 empty] | 4EL1 |  |  |  |  | 245
[5 empty] | 4EL2 |  |  |  |  | 246
[5 empty] | 0EL1 |  |  |  |  | 247
[5 empty] | 0EL2 |  |  |  |  | 248
[5 empty] | 0ST2 |  |  |  |  | 249
251
253
255
260A
260B
260C
260E
260F
260G
260H
260J
261
270
271A
271B
271C
271E
271F
280
2EL1
2ST1
2ST2
2ST3
300A
300B
300D
300E
300F
300G
301A
301B
301C
301D
301E
301F
301G
302
303
305
310
311
311A
311B
311C
311D
311E
311F
311G
311H
320
326
328
330
331
332
333
334
335
336
337
338
339
340
341
342
343
344
345
346
347
348
349
351
353
355
360
360A
360B
360C
360D
360E
361
361A
361B
361C
361D
361E
361F
361G
361H
361K
361L
361M
361N
370
371
380
381
381A
381B
381C
381D
381E
381F
381G
390
390A
390B
390C
390D
390E
391
391A
391B
391C
3EL1
3ST1
3ST2
3ST3
400
ROOF
071B
071C
071D
071E
271T
4EL1
1ST3
260K
260L
260M
260N
260O
260P
260Q
260R
260S
260T
260U
260V
271G
271H
271J
271K
271L
271M
271N
271O
271P
271Q
271R
271S
271U
321A
321B
401
402
403
404
4ST2
4ST3
188A

## Status
STATUS CODE | DESCRIPTION
ACTIVE | Owned and In Service/Operating
INACTIVE | Not in use, Retired, or Disposed
DEMO | Demolished
TOS | Temporarily Out of Service

## Uniformat
Level 1 Major Group Elements |  | Level 2 Group Elements |  | Level 3 Individual Elements
CODE (LV1) | DESCRIPTION | CODE (LV2) | DESCRIPTION3 | CODE (LV3) | DESCRIPTION5
A | SUBSTRUCTURE | A10 | Foundations | A1010 | Standard Foundations
|  |  |  | A1020 | Special Foundations
|  |  |  | A1030 | Slab on Grade
|  | A20 | Basement Construction | A2010 | Basement Excavation
|  |  |  | A2020 | Basement Walls
B | SHELL | B10 | Superstructure | B1010 | Floor Construction
|  |  |  | B1020 | Roof Construction
|  | B20 | Exterior Enclosure | B2010 | Exterior Walls
|  |  |  | B2020 | Exterior Windows
|  |  |  | B2030 | Exterior Doors
|  | B30 | Roofing | B3010 | Roof Coverings
|  |  |  | B3020 | Roof Openings
C | INTERIORS | C10 | Interior Construction | C1010 | Partitions
|  |  |  | C1020 | Interior Doors
|  |  |  | C1030 | Fittings
|  | C20 | Stairs | C2010 | Stair Construction
|  |  |  | C2020 | Stair Finishes
|  | C30 | Interior Finishes | C3010 | Wall Finishes
|  |  |  | C3020 | Floor Finishes
|  |  |  | C3030 | Ceiling Finishes
D | SERVICES | D10 | Conveying | D1010 | Elevators & Lifts
|  |  |  | D1020 | Escalators & Moving Walks
|  |  |  | D1090 | Other Conveying Systems
|  | D20 | Plumbing | D2010 | Plumbing Fixtures
|  |  |  | D2020 | Domestic Water Distribution
|  |  |  | D2030 | Sanitary Waste
|  |  |  | D2040 | Rain Water Drainage
|  |  |  | D2090 | Other Plumbing Systems
|  | D30 | HVAC | D3010 | Energy Supply
|  |  |  | D3020 | Heat Generating Systems
|  |  |  | D3030 | Cooling Generating Systems
|  |  |  | D3040 | Distribution Systems
|  |  |  | D3050 | Terminal & Package Units
|  |  |  | D3060 | Controls & Instrumentation
|  |  |  | D3070 | Systems Testing & Balancing
|  |  |  | D3090 | Other HVAC Systems & Equipment
|  | D40 | Fire Protection | D4010 | Sprinklers
|  |  |  | D4020 | Standpipes
|  |  |  | D4030 | Fire Protection Specialties
|  |  |  | D4090 | Other Fire Protection Systems
|  | D50 | Electrical | D5010 | Electrical Service & Distribution
|  |  |  | D5020 | Lighting and Branch Wiring
|  |  |  | D5030 | Communications & Security
|  |  |  | D5090 | Other Electrical Systems
E | EQUIPMENT & FURNISHINGS | E10 | Equipment | E1010 | Commercial Equipment
|  |  |  | E1020 | Institutional Equipment
|  |  |  | E1030 | Vehicular Equipment
|  |  |  | E1090 | Other Equipment
|  | E20 | Furnishings | E2010 | Fixed Furnishings
|  |  |  | E2020 | Movable Furnishings
F | SPECIAL CONSTRUCTION & DEMOLITION | F10 | Special Construction | F1010 | Special Structures
|  |  |  | F1020 | Integrated Construction
|  |  |  | F1030 | Special Construction Systems
|  |  |  | F1040 | Special Facilities
|  |  |  | F1050 | Special Controls and
Instrumentation
|  | F20 | Selective Building | F2010 | Building Elements Demolition
|  |  | Demolition | F2020 | Hazardous Components
Abatement
G | BUILDING SITEWORK | G10 | Site Preparation | G1010 | Site Clearing
|  |  |  | G1020 | Site Demolition and Relocations
|  |  |  | G1030 | Site Earthwork
|  |  |  | G1040 | Hazardous Waste Remediation
|  | G20 | Site Improvements | G2010 | Roadways
|  |  |  | G2020 | Parking Lots
|  |  |  | G2030 | Pedestrian Paving
|  |  |  | G2040 | Site Development
|  |  |  | G2050 | Landscaping
|  | G30 | Site Mechanical | G3010 | Water Supply
|  |  |  | G3020 | Sanitary Sewer
|  |  |  | G3030 | Storm Sewer
|  |  |  | G3040 | Heating Distribution
|  |  |  | G3050 | Cooling Distribution
|  |  |  | G3060 | Fuel Distribution
|  |  |  | G3090 | Other Site Mechanical Utilities
|  | G40 | Site Electrical | G4010 | Electrical Distribution
|  |  |  | G4020 | Site Lighting
|  |  |  | G4030 | Site Communications & Security
|  |  |  | G4090 | Other Site Electrical Utilities
|  | G90 | Other Site Construction | G9010 | Service and Pedestrian Tunnels
|  |  |  | G9090 | Other Site Systems & Equipment

## Useful Life Table
BOMA Preventative Maintenance Manual, Expected Useful Life table |  | https://deptofcommerce.app.box.com/s/g38qhzhfpbrwlrbsfzc37fjk9dw0rflx
Uniformat Code | Description | Detailed Description | Useful Life
B2010 | Exterior walls | Siding: painted wood | 30
B2010 | Exterior walls | Siding: metal | 30
B2010 | Exterior walls | Siding: vinyl | 30
B2010 | Exterior walls | Siding: masonry | 75
B2010 | Exterior walls | Siding: stone | 100
B2010 | Exterior walls | Building Façade: metal curtain wall | 50
B2010 | Exterior walls | Building Façade: glass curtain wall | 50
B2010 | Exterior walls | Building Façade: precast panels | 35
B2010 | Exterior walls | Building Façade: stone veneer | 50
B2010 | Exterior walls | Building Façade: windows (operable or gasketed) | 30
B2030 | Exterior doors | Door hardware: entry lock sets | 7
B2030 | Exterior doors | Door hardware: closures | 7
B2030 | Exterior doors | Door hardware: automatic doors | 5
B3010 | Roofs/roofing | Roofing: 4-ply built up, asphalt, flat, no slope | 18
B3010 | Roofs/roofing | Roofing: 4-ply built up, asphalt, sloped | 25
B3010 | Roofs/roofing | Roofing: 4-ply built up, cold tar | 35
B3010 | Roofs/roofing | Roofing: 4-ply built up, hot-applied rubberized asphalt (membrane) | 30
B3010 | Roofs/roofing | Roofing: 2-ply modified bitumen (mopped down), flat, no slope | 15
B3010 | Roofs/roofing | Roofing: 2-ply modified bitumen (mopped down), flat, sloped | 20
B3010 | Roofs/roofing | Roofing: 1-ply EPDM, flat, no slope | 15
B3010 | Roofs/roofing | Roofing: 1-ply EPDM, flat, sloped | 20
B3010 | Roofs/roofing | Roofing: 1-ply, thermoplastic (Hypalon, PVC) | 20
B3010 | Roofs/roofing | Roofing: 1-ply, modified Bitumen (touched on), flat, no slope | 10
B3010 | Roofs/roofing | Roofing: 1-ply, modified Bitumen (touched on), sloped | 15
B3010 | Roofs/roofing | Metal Roofing: structural roof panels (pre-finished galvanized steel) | 25
B3010 | Roofs/roofing | Metal Roofing: premanufactured architectural roof panels (prefinished aluminum or galvanized steel) | 25
B3010 | Roofs/roofing | Metal Roofing: Custom Fabricated Standing Seam Roofing (Copper, Lead Coated Copper, Terne Coated Stainless Steel) | 75
B3010 | Roofs/roofing | Metal Roofing: Custom Fabricated Flat Seam (Copper, Lead Coated Copper, Terne Coated Stainless Steel) | 50
B3010 | Roofs/roofing | Asphalt roofing: 15-year | 15
B3010 | Roofs/roofing | Asphalt roofing: 20-year | 20
B3010 | Roofs/roofing | Asphalt roofing: 25-year | 25
B3010 | Roofs/roofing | Asphalt roofing: 30-year | 30
B3010 | Roofs/roofing | Slate roofing: S-1 | 100
B3010 | Roofs/roofing | Slate roofing: S-2 | 75
B3010 | Roofs/roofing | Slate roofing: S-3 | 50
B3010 | Roofs/roofing | Clay/concrete tile roofing | 50
B3010 | Roofs/roofing | Roofing: spray-on polyurethane foam | 10
C3010 | Interior Wall Finishes | Wall coverings: vinyl | 10
C3010 | Interior Wall Finishes | Wall coverings: paint | 5
C3010 | Interior Wall Finishes | Wall coverings: wall paper | 4
C3010 | Interior Wall Finishes | Wall coverings: two-part epoxy | 15
C3010 | Interior Wall Finishes | Wall coverings: fabric | 5
C3010 | Interior Wall Finishes | Wall coverings: wood finish | 15
C3020 | Interior Floor Finishes | Flooring: vinyl tile or sheet | 12
C3020 | Interior Floor Finishes | Flooring: carpet, broad loom | 5
C3020 | Interior Floor Finishes | Flooring: carpet, tiles | 5
C3020 | Interior Floor Finishes | Flooring: carpet, loop pile | 15
C3020 | Interior Floor Finishes | Flooring: epoxy coating | 10
C3020 | Interior Floor Finishes | Flooring: granite | 75
C3020 | Interior Floor Finishes | Flooring: marble | 50
C3020 | Interior Floor Finishes | Flooring: terazzo | 50
C3020 | Interior Floor Finishes | Flooring: hardwood, finished | 10
C3020 | Interior Floor Finishes | Flooring: hardwood substrate | 50
C3020 | Interior Floor Finishes | Flooring: concrete | 50
C3030 | Interior Ceiling Finishes | Ceilings: plaster/dry wall w/ skim coat | 30
C3030 | Interior Ceiling Finishes | Ceilings: suspended, spline system | 20
C3030 | Interior Ceiling Finishes | Ceilings: suspended, lay-in system | 25
C3030 | Interior Ceiling Finishes | Ceilings: suspended, ceiling tiles | 13
C3030 | Interior Ceiling Finishes | Ceilings: metal | 25
C3030 | Interior Ceiling Finishes | Ceilings: wood | 30
D1010 | Elevators/lifts | Elevator: hydraulic, underground cylinder, dry location | 15
D1010 | Elevators/lifts | Elevator: hydraulic, car and pump unit | 35
D1010 | Elevators/lifts | Elevator: traction | 50
D1010 | Elevators/lifts | Elevator: geared traction | 35
D1010 | Elevators/lifts | Elevator: cab interior finish | 10
D1010 | Elevators/lifts | Elevator: carpet | 0.5
D1010 | Elevators/lifts | Controller: electromechanical relay-based | 30
D1010 | Elevators/lifts | Controller: computer-based | 20
D1010 | Elevators/lifts | Elevator door operator: passenger | 20
D1010 | Elevators/lifts | Elevator door operator: freight or service used for carts | 10
D1090 | Interior Conveyances, other | Escalator: dry location, not for mass transit | 40
D1090 | Interior Conveyances, other | Escalator: wet location, and/or for mass transit | 20
D1090 | Interior Conveyances, other | Lift: wheelchair and/or stairway | 25
D2010 | Interior Plumbing Fixtures | Plumbing: flush valves | 12
D2010 | Interior Plumbing Fixtures | Plumbing: commercial faucet | 7
D2010 | Interior Plumbing Fixtures | Plumbing: commercial water closet | 30
D2010 | Interior Plumbing Fixtures | Plumbing: commercial urinal | 30
D2010 | Interior Plumbing Fixtures | Plumbing: commercial sink | 30
D2010 | Interior Plumbing Fixtures | Plumbing: commercial refridgerated drinking fountain | 15
D2020 | Domestic Water systems: interior | Water heater, long warranty: electric, normal use | 15
D2020 | Domestic Water systems: interior | Water heater, long warranty: electric, heavy use or tankless | 10
D2020 | Domestic Water systems: interior | Water heater, long warranty: oil-fired | 18
D2020 | Domestic Water systems: interior | Water heater, long warranty: gas-fired, normal use | 15
D2020 | Domestic Water systems: interior | Water heater, long warranty: gas-fired, heavy use or tankless | 10
D2020 | Domestic Water systems: interior | Water heater, long warranty: solar thermal collector | 20
D2020 | Domestic Water systems: interior | Plumbing pump: base-mounted | 25
D2020 | Domestic Water systems: interior | Plumbing pump: in-line | 15
D2020 | Domestic Water systems: interior | Plumbing pump: sewage ejector | 10
D2020 | Domestic Water systems: interior | Plumbing pump: sump-submerged or pedestal | 10
D2020 | Domestic Water systems: interior | Plumbing pump: well-submerged | 10
D2020 | Domestic Water systems: interior | Plumbing backflow prevention: light duty | 10
D2020 | Domestic Water systems: interior | Plumbing backflow prevention: heavy duty (main service) | 30
D2020 | Domestic Water systems: interior | Domestic Water hot/cold, copper, plastic piping | 30
D2020 | Domestic Water systems: interior | Water softeners | 25
D2030 | Interior Sanitary Waste Water Systems | Domestic waste water piping: PVC or cast iron | 30
D2030 | Interior Sanitary Waste Water Systems | Kitchen waste water piping | 20
D3010 | HVAC Energy Supply Systems | Ground-source heat pump exchange loops | 40
D3010 | HVAC Energy Supply Systems | Gas piping: fuel gas, threaded | 30
D3010 | HVAC Energy Supply Systems | Gas piping: fuel gas, welded | 40
D3010 | HVAC Energy Supply Systems | Gas piping: medical gas supply | 40
D3020 | HVAC Heating Systems | Boiler: hot water, steel water-tube | 30
D3020 | HVAC Heating Systems | Boiler: hot water, steel fire-tube | 30
D3020 | HVAC Heating Systems | Boiler: hot water, cast iron | 30
D3020 | HVAC Heating Systems | Boiler: hot water, electric | 25
D3020 | HVAC Heating Systems | Boiler: hot water, condensing | 15
D3020 | HVAC Heating Systems | Boiler: Steam, cast iron | 30
D3020 | HVAC Heating Systems | Boiler: Steam, steel fire-tube | 25
D3020 | HVAC Heating Systems | Boiler: Steam, steel water-tube | 28
D3020 | HVAC Heating Systems | Burners | 18
D3020 | HVAC Heating Systems | Energy Recovery Air to Air | 12
D3020 | HVAC Heating Systems | Energy Recovery Heat Pipe | 20
D3020 | HVAC Heating Systems | Energy Recovery Water | 12
D3020 | HVAC Heating Systems | Energy Recovery Wheel | 15
D3020 | HVAC Heating Systems | Furnaces: condensing | 15
D3020 | HVAC Heating Systems | Furnaces: gas or oil | 18
D3020 | HVAC Heating Systems | Heat Exchangers, commercial shell & tube: steam to domestic water | 13
D3020 | HVAC Heating Systems | Heat Exchangers, commercial shell & tube: steam to heating water | 20
D3020 | HVAC Heating Systems | Heat Exchangers, commercial shell & tube: water to domestic water | 15
D3020 | HVAC Heating Systems | Heat Exchangers, commercial shell & tube: water to water | 25
D3020 | HVAC Heating Systems | HVAC Coils: electric | 12
D3020 | HVAC Heating Systems | HVAC Coils: water, steam | 20
D3020 | HVAC Heating Systems | Radiant Heater: gas | 18
D3020 | HVAC Heating Systems | Radiant heaters: electric | 10
D3020 | HVAC Heating Systems | Radiant heaters: hot water | 25
D3020 | HVAC Heating Systems | Unit Heaters: gas | 13
D3020 | HVAC Heating Systems | Unit Heaters: electric | 15
D3020 | HVAC Heating Systems | Unit Heaters: hot water or steam | 20
D3030 | HVAC Cooling Systems | Air Conditioner: window unit | 10
D3030 | HVAC Cooling Systems | Air Conditioner: res. single or split package | 15
D3030 | HVAC Cooling Systems | Air Conditioner: commercial | 10
D3030 | HVAC Cooling Systems | Air Conditioner: water-cooled package | 20
D3030 | HVAC Cooling Systems | Air Conditioner: computer room unit | 15
D3030 | HVAC Cooling Systems | Air Conditioner: rooftop, single zone | 18
D3030 | HVAC Cooling Systems | Air Conditioner: rooftop, multizone | 18
D3030 | HVAC Cooling Systems | Air Conditioner: rooftop, VAV | 20
D3030 | HVAC Cooling Systems | Chiller: absorption | 30
D3030 | HVAC Cooling Systems | Chiller: centrifugal | 20
D3030 | HVAC Cooling Systems | Chiller: reciprocating | 20
D3030 | HVAC Cooling Systems | Chiller: screw | 20
D3030 | HVAC Cooling Systems | Chiller: scroll | 15
D3030 | HVAC Cooling Systems | Condensers: air-cooled | 20
D3030 | HVAC Cooling Systems | Condensers: evaporative | 15
D3030 | HVAC Cooling Systems | Cooling tower: ceramic | 35
D3030 | HVAC Cooling Systems | Cooling Tower: fiberglass | 35
D3030 | HVAC Cooling Systems | Cooling Tower: fill media | 15
D3030 | HVAC Cooling Systems | Cooling Tower: galvanized or coated steel | 18
D3030 | HVAC Cooling Systems | Cooling Tower: stainless steel | 25
D3030 | HVAC Cooling Systems | Cooling Tower: wood | 20
D3030 | HVAC Cooling Systems | HVAC Coils: cooling, dehumidifying | 12
D3030 | HVAC Cooling Systems | HVAC Coils: direct expansion | 18
D3030 | HVAC Cooling Systems | Residential packaged or split A/C | 15
D3040 | HVAC Distribution Systems | Air Handler: built-up heavy duty | 30
D3040 | HVAC Distribution Systems | Air Handler: packaged, medium duty | 25
D3040 | HVAC Distribution Systems | Air Handler: severe duty or 100% outside air | 20
D3040 | HVAC Distribution Systems | Air Terminal: Fan coil units | 20
D3040 | HVAC Distribution Systems | Air Terminal: grills, diffusers, registers, heavy gauge, coated | 30
D3040 | HVAC Distribution Systems | Air Terminal: grills, diffusers, registers, perforated or light guage | 15
D3040 | HVAC Distribution Systems | Air Terminal: Induction units | 35
D3040 | HVAC Distribution Systems | Air Terminals: CAV boxes | 25
D3040 | HVAC Distribution Systems | Air Terminals: Double duct boxes | 25
D3040 | HVAC Distribution Systems | Air Terminals: Fan power VAV boxes | 17
D3040 | HVAC Distribution Systems | Air Terminals: Variable volume temperature boxes | 15
D3040 | HVAC Distribution Systems | Air Terminals: VAV boxes, cooling only | 25
D3040 | HVAC Distribution Systems | Dampers: fixed or fusible link | 30
D3040 | HVAC Distribution Systems | Dampers: operable or automatic | 20
D3040 | HVAC Distribution Systems | Ductwork: fiberglass | 15
D3040 | HVAC Distribution Systems | Ductwork: flexible round | 10
D3040 | HVAC Distribution Systems | Ductwork: galvanized steel, aluminum, & black iron | 30
D3040 | HVAC Distribution Systems | Fans: axial | 20
D3040 | HVAC Distribution Systems | Fans: centrifugal | 25
D3040 | HVAC Distribution Systems | Fans: propeller | 15
D3040 | HVAC Distribution Systems | Insulation: blanket | 25
D3040 | HVAC Distribution Systems | Insulation: molded | 20
D3040 | HVAC Distribution Systems | Motor starters: in dry, non-corrosive area | 25
D3040 | HVAC Distribution Systems | Motor starters: in wet or corrosive areas | 10
D3040 | HVAC Distribution Systems | Motors: electric, w/ soft start | 25
D3040 | HVAC Distribution Systems | Motors: electric, w/o soft start | 18
D3040 | HVAC Distribution Systems | Heat Exchanger: Plate and Frame | 25
D3040 | HVAC Distribution Systems | HVAC pumps: base-mounted | 25
D3040 | HVAC Distribution Systems | HVAC pumps: condensate | 15
D3040 | HVAC Distribution Systems | HVAC pumps: in-line | 15
D3040 | HVAC Distribution Systems | HVAC pumps: sump-submerged | 10
D3040 | HVAC Distribution Systems | HVAC pumps: well-submerged | 10
D3040 | HVAC Distribution Systems | Reciprocating air compressors | 15
D3040 | HVAC Distribution Systems | Reciprocating Engines: backup service | 20
D3040 | HVAC Distribution Systems | Reciprocating Engines: continuous service | 5
D3040 | HVAC Distribution Systems | Reciprocating Engines: steam turbines | 30
D3040 | HVAC Distribution Systems | Residential Immersion Coil | 25
D3040 | HVAC Distribution Systems | Fan, ventilating: kitchen or other soiled exhaust | 15
D3040 | HVAC Distribution Systems | Fan, ventilating: roof mounted | 20
D3040 | HVAC Distribution Systems | Heating/cooling piping systems: above ground | 30
D3040 | HVAC Distribution Systems | Flue/chimney: metal, incl. breeching | 20
D3040 | HVAC Distribution Systems | Flue/chimney: steel | 30
D3040 | HVAC Distribution Systems | Flue/chimney: masonry | 50
D3040 | HVAC Distribution Systems | Electrical in Dry, Noncorrosive Locations (Except for Equipment Designed to be Outdoors or in Wet Locations): motors | 18
D3040 | HVAC Distribution Systems | Electrical in Dry, Noncorrosive Locations (Except for Equipment Designed to be Outdoors or in Wet Locations): motor control center | 30
D3050 | HVAC Terminal and Package Units | Heat pump: res. air-to-air | 12
D3050 | HVAC Terminal and Package Units | Heat pump: commercial air-to-air | 15
D3050 | HVAC Terminal and Package Units | Heat pump: commercial water-to-air | 18
D3050 | HVAC Terminal and Package Units | Heater: steam or HW, cast iron convector | 50
D3050 | HVAC Terminal and Package Units | Heater: steam or HW fin tube | 15
D3060 | HVAC Controls and Instrumentation | Control Sensors: air flow | 10
D3060 | HVAC Controls and Instrumentation | Control Sensors: humidity, CO2 | 5
D3060 | HVAC Controls and Instrumentation | Control Sensors: temperature | 20
D3060 | HVAC Controls and Instrumentation | Control Sensors: water flow | 5
D3060 | HVAC Controls and Instrumentation | Controls: computer front end | 15
D3060 | HVAC Controls and Instrumentation | Controls: electric | 20
D3060 | HVAC Controls and Instrumentation | Controls: electronic | 20
D3060 | HVAC Controls and Instrumentation | Controls: pneumatic | 18
D3060 | HVAC Controls and Instrumentation | Valve Actuators: hydraulic | 15
D3060 | HVAC Controls and Instrumentation | Valve Actuators: motorized electric | 18
D3060 | HVAC Controls and Instrumentation | Valve Actuators: pneumatic | 20
D3060 | HVAC Controls and Instrumentation | Valve Actuators: self-contained | 10
D3090 | HVAC Other Systems and Equipment | Air Washer/Humidifiers: pan, wheel, or wetted element | 8
D3090 | HVAC Other Systems and Equipment | Air Washer/Humidifiers: spray | 12
D3090 | HVAC Other Systems and Equipment | Air Washer/Humidifiers: steam | 15
D4010 | Fire Sprinkler systems | Sprinkler systems: heads | 25
D4010 | Fire Sprinkler systems | Fire pumps: electric motor driven | 25
D4010 | Fire Sprinkler systems | Fire pumps: engine driven | 20
D4010 | Fire Sprinkler systems | Sprinkler systems: piping systems | 40
D4010 | Fire Sprinkler systems | Sprinkler systems: equipment and devices (flow switch, dry pipe valve, etc) | 20
D4090 | Fire Alarm systems | Fire alarm systems: activation devices (pull stations, smoke detectors, etc) | 10
D4090 | Fire Alarm systems | Fire alarm systems: notification devices (AV horn, strobe) | 15
D4090 | Fire Alarm systems | Fire alarm systems: control panels | 15
D4090 | Fire Alarm systems | Fire alarm systems: wiring | 30
D5010 | Building Electrical Svc & Distribution | Electrical in Dry, Noncorrosive Locations (Except for Equipment Designed to be Outdoors or in Wet Locations): transformers, oil-filled | 30
D5010 | Building Electrical Svc & Distribution | Electrical in Dry, Noncorrosive Locations (Except for Equipment Designed to be Outdoors or in Wet Locations): transformers, dry | 30
D5010 | Building Electrical Svc & Distribution | Electrical in Dry, Noncorrosive Locations (Except for Equipment Designed to be Outdoors or in Wet Locations): Automatic transfer switch | 25
D5010 | Building Electrical Svc & Distribution | Electrical in Dry, Noncorrosive Locations (Except for Equipment Designed to be Outdoors or in Wet Locations): power panels - light & power distribution boards | 30
D5010 | Building Electrical Svc & Distribution | Electrical in Dry, Noncorrosive Locations (Except for Equipment Designed to be Outdoors or in Wet Locations): switchgear & service entrance equipment | 40
D5010 | Building Electrical Svc & Distribution | Electrical in Dry, Noncorrosive Locations (Except for Equipment Designed to be Outdoors or in Wet Locations): circuit breakers | 30
D5010 | Building Electrical Svc & Distribution | Electrical in Dry, Noncorrosive Locations (Except for Equipment Designed to be Outdoors or in Wet Locations): GFCI switch | 25
D5010 | Building Electrical Svc & Distribution | Electrical in Dry, Noncorrosive Locations (Except for Equipment Designed to be Outdoors or in Wet Locations): wire & cable, < 600V | 40
D5010 | Building Electrical Svc & Distribution | Electrical in Dry, Noncorrosive Locations (Except for Equipment Designed to be Outdoors or in Wet Locations): wire & cable, > 600V | 40
D5010 | Building Electrical Svc & Distribution | Electrical in Dry, Noncorrosive Locations (Except for Equipment Designed to be Outdoors or in Wet Locations): solar PV panels | 20
D5020 | Building Lighting and Branch Wiring | Electrical in Dry, Noncorrosive Locations (Except for Equipment Designed to be Outdoors or in Wet Locations): light fixtures | 20
D5020 | Building Lighting and Branch Wiring | Electrical in Dry, Noncorrosive Locations (Except for Equipment Designed to be Outdoors or in Wet Locations): branch circuit wiring and devices | 30
D5020 | Building Lighting and Branch Wiring | Electrical in Dry, Noncorrosive Locations (Except for Equipment Designed to be Outdoors or in Wet Locations): lighting protection | 40
D5030 | Building Electrical Communications and Security | Security systems: activation devices (access entry, motion sensor, etc) | 10
D5030 | Building Electrical Communications and Security | Security systems: notification devices (horn, dialer) | 15
D5030 | Building Electrical Communications and Security | Security systems: control panels | 15
D5030 | Building Electrical Communications and Security | CCTV: monitors | 53
D5030 | Building Electrical Communications and Security | CCTV: pan and tilt motors | 53
D5030 | Building Electrical Communications and Security | CCTV: cameras | 65
D5030 | Building Electrical Communications and Security | CCTV: computer control | 10
D5090 | Building Electrical Other | Electrical in Dry, Noncorrosive Locations (Except for Equipment Designed to be Outdoors or in Wet Locations): UPS - battery | 10
D5090 | Building Electrical Other | Electrical in Dry, Noncorrosive Locations (Except for Equipment Designed to be Outdoors or in Wet Locations): UPS - rotary | 15
D5090 | Building Electrical Other | Electrical in Dry, Noncorrosive Locations (Except for Equipment Designed to be Outdoors or in Wet Locations): batteries | 5
D5090 | Building Electrical Other | Electrical in Dry, Noncorrosive Locations (Except for Equipment Designed to be Outdoors or in Wet Locations): emergency engine generator set | 20
D5090 | Building Electrical Other | Battery standby power supply | 5
E1020 | NON-PROGRAM INSTITUTIONAL EQUIPMENT/FURNISHINGS | Compressed air piping | 20
E1020 | NON-PROGRAM INSTITUTIONAL EQUIPMENT/FURNISHINGS | Air compressors and vaccuum pumps | 15
F1000 | Special Construction and Structures | Oil storage tank: w/ corrosion protection, above ground | 25
F1000 | Special Construction and Structures | Oil storage tank: w/ corrosion protection, underground | 20
F1000 | Special Construction and Structures | Oil storage tank: w/ corrosion protection, underground, FRP coated steel | 30
G2020 | Site Improvements | Outdoor paved surfaces at grade or topmost level | 30
G2020 | Site Improvements | Outdoor paving with roof, no side wall, covering | 40