1. GENERAL
   1. SUMMARY
      1. Section Includes:
         1. Structural steel.
         2. Metal framing system components.
      2. General Structural Notes on Drawings also apply to work of this Section.
      3. Field Welding is subject to strict compliance with UW Medical Center Safety and Fire Watch requirements. Coordinate work with Owner.
   2. SUBMITTALS
      1. Comply with requirements of Section 01 33 00 'Submittal Procedures'.
      2. Shop Drawings: Show fabrication of structural-steel components.
         1. Include details of cuts, connections, splices, camber, holes, and other pertinent data.
         2. Indicate welds by standard AWS symbols, distinguishing between shop and field welds, and show size, length, and type of each weld. Show backing bars that are to be removed and supplemental fillet welds where backing bars are to remain.
         3. Indicate type, size, and length of bolts, distinguishing between shop and field bolts. Identify pre-tensioned and slip-critical high-strength bolted connections.
      3. Qualification Data: For qualified installer and fabricator.
      4. Welding certificates.
      5. Paint Compatibility Certificates: From manufacturers of topcoats applied over shop primers, certifying that shop primers are compatible with topcoats.
      6. Mill test reports for structural steel, including chemical and physical properties.
      7. Product Test Reports: For the following:

Revise list below to suit Project. Insert alternative design bolts if required.

* + - 1. Bolts, nuts, and washers including mechanical properties and chemical analysis.
      2. Shop primers.
    1. Source quality-control reports.
  1. QUALITY ASSURANCE

Retain first paragraph below if AISC certification of fabricator is required. Category STD is for steel building structures; other categories in fabricator certification program are for bridges.

* + 1. Fabricator Qualifications: A qualified fabricator that participates in the AISC Quality Certification Program and is designated an AISC-Certified Plant, Category STD.
    2. Installer Qualifications: A qualified installer who participates in the AISC Quality Certification Program and is designated an AISC-Certified Erector, Category CSE.
    3. Welding Qualifications: Qualify procedures and personnel according to AWS D1.1/D1.1M, "Structural Welding Code - Steel."
    4. Comply with applicable provisions of the following specifications and documents:

Retain references in subparagraphs below if applicable. Insert others to suit Project.

* + - 1. AISC 303.
      2. AISC 360.
      3. RCSC's "Specification for Structural Joints Using ASTM A 325 or A 490 Bolts."
  1. DELIVERY, STORAGE, AND HANDLING
     1. Store materials to permit easy access for inspection and identification. Keep steel members off ground and spaced by using pallets, dunnage, or other supports and spacers. Protect steel members and packaged materials from corrosion and deterioration.
        1. Do not store materials on structure in a manner that might cause distortion, damage, or overload to members or supporting structures. Repair or replace damaged materials or structures as directed.
     2. Store fasteners in a protected place in sealed containers with manufacturer's labels intact.
        1. Fasteners may be repackaged provided Owner's testing and inspecting agency observes repackaging and seals containers.
        2. Clean and re-lubricate bolts and nuts that become dry or rusty before use.
  2. COORDINATION
     1. Coordinate selection of shop primers with topcoats to be applied over them. Comply with paint and coating manufacturers' recommendations to ensure that shop primers and topcoats are compatible with one another.
     2. Coordinate installation of anchorage items to be embedded in or attached to other construction without delaying the Work. Provide setting diagrams, sheet metal templates, instructions, and directions for installation.

1. PRODUCTS
   1. STRUCTURAL-STEEL MATERIALS

Retain one of two "Recycled Content of Steel Products" paragraphs below if required for LEED Credit MR 4. USGBC allows a default value of 25 percent to be used for steel, without documentation; higher percentages can be claimed if they are supported by appropriate documentation. The Steel Recycling Institute indicates that hollow structural shapes, pipe, and steel plates typically have 23 percent postconsumer recycled content and 1.5 percent preconsumer recycled content; and rolled structural shapes typically have 57.5 percent postconsumer recycled content and 6.5 percent preconsumer recycled content.

* + 1. Recycled Content of Steel Products: Postconsumer recycled content plus one-half of pre-consumer recycled content not less than 25%.
    2. Channels, Angles, Shapes: ASTM A 36/A 36M, Fy=36 KSI
    3. Plate and Bar: ASTM A 36/A 36M.
    4. Hollow Structural Sections (HSS): ASTM A500 Grade B, Fy=46 KSI.
    5. Welding Electrodes: Comply with AWS requirements.
  1. THREADED RODS

If corrosion-resisting (weathering) steel is used, change Type 1 bolts and washers to Type 3 and Grade C nuts to Grade C3 (Class 8S to Class 8S3) in first paragraph below. If using bolts in first paragraph below for some connections and ASTM A 490 (ASTM A 490M) bolts for others, indicate location of each on Drawings.

Retain subparagraph below if applicable. If corrosion-resisting (weathering) steel is used, change Type 325 to Type 325-3; ASTM F 959M does not include a designation for corrosion-resistant steel.

If corrosion-resisting (weathering) steel is used, change Type 1 bolts and washers to Type 3 and Grade DH nuts to Grade DH3 (Class 10S to Class 10S3) in first paragraph below. If using bolts in first paragraph below for some connections and ASTM A 325 (ASTM A 325M) bolts in paragraph above for others, indicate location of each on Drawings. Retain option below if applicable.

* + 1. ASTM F1554, Grade 36 or 55.
  1. BOLTS, CONNECTORS, AND ANCHORS

If corrosion-resisting (weathering) steel is used, change Type 1 bolts and washers to Type 3 and Grade C nuts to Grade C3 (Class 8S to Class 8S3) in first paragraph below. If using bolts in first paragraph below for some connections and ASTM A 490 (ASTM A 490M) bolts for others, indicate location of each on Drawings.

Retain subparagraph below if applicable. If corrosion-resisting (weathering) steel is used, change Type 325 to Type 325-3; ASTM F 959M does not include a designation for corrosion-resistant steel.

If corrosion-resisting (weathering) steel is used, change Type 1 bolts and washers to Type 3 and Grade DH nuts to Grade DH3 (Class 10S to Class 10S3) in first paragraph below. If using bolts in first paragraph below for some connections and ASTM A 325 (ASTM A 325M) bolts in paragraph above for others, indicate location of each on Drawings. Retain option below if applicable.

* + 1. Zinc-Coated High-Strength Bolts, Nuts, and Washers: ASTM A 325 (ASTM A 325M), Type 1, heavy-hex steel structural bolts; ASTM A 563, Grade DH (ASTM A 563M, Class 10S) heavy-hex carbon-steel nuts; and ASTM F 436 (ASTM F 436M), Type 1, hardened carbon-steel washers.
       1. Finish: Hot-dip zinc coating.
    2. Expansion Bolts, Adhesive Bolts and Screw Anchors: As indicated in General Structural Notes on the Contract Drawings.
  1. PRIMER

Retain "Low-Emitting Materials" Paragraph below if required for LEED for Schools.

Insert proprietary primers if required as part of special coating or painting system. Coordinate primer selection with surface preparation and topcoats, requirements for slip-critical joints, and limitations of sprayed fire-resistive materials. Insert color if required.

Verify that fabricator offers primers that meet limitations and characteristics in first paragraph below. Fabricator's standard primer requires SSPC-SP 2 surface preparation or better and usually provides minimal protection.

* + 1. Primer: Fabricator's standard lead- and chromate-free, non-asphaltic, rust-inhibiting primer complying with Master Painters Institute (MPI) Approved Products List #79 and compatible with topcoat.
  1. GROUT

Retain "Low-Emitting Materials" Paragraph below if required for LEED for Schools.

Insert proprietary primers if required as part of special coating or painting system. Coordinate primer selection with surface preparation and topcoats, requirements for slip-critical joints, and limitations of sprayed fire-resistive materials. Insert color if required.

Verify that fabricator offers primers that meet limitations and characteristics in first paragraph below. Fabricator's standard primer requires SSPC-SP 2 surface preparation or better and usually provides minimal protection.

* + 1. ASTM C1107-00, premixed non shrink type. 5,000 PSI Minimum, 7-day cure strength.
       1. Masterflow 928 High-precision mineral-aggregate grout by BASF,
       2. WR Meadows 1428 HP Mineral Aggregate-Based Precision Grout
       3. or Approved Equal.
  1. METAL STRUT CHANNEL SYSTEM
     1. Products: Subject to compliance with requirements, provide one of the following as indicated on the Drawings:
        1. Metal Framing Strut Channel System and Accessories
           1. Basis of Design: Unistrut.
     2. Steel: Pre-Galvanized; 12GA (2.7 mm), 14GA (1.9 mm) and 16 GA (1.5 mm). ASTM A653 SS GR 33.
     3. Finishes: Hot-dipped Galvanized (HG) conforming to ASTM A123 or A153.
  2. FABRICATION
     1. Structural Steel: Fabricate and assemble in shop to greatest extent possible. Fabricate according to AISC's "Code of Standard Practice for Steel Buildings and Bridges" and AISC 360.
        1. Mark and match-mark materials for field assembly.
        2. Complete structural-steel assemblies, including welding of units, before starting shop-priming operations.
     2. Thermal Cutting: Perform thermal cutting by machine to greatest extent possible.
        1. Plane thermally cut edges to be welded to comply with requirements in AWS D1.1/D1.1M.
     3. Bolt Holes: Cut, drill, or punch standard bolt holes perpendicular to metal surfaces.
     4. Finishing: Accurately finish ends of columns and other members transmitting bearing loads.
  3. SHOP CONNECTIONS

Retain option in paragraph below for "High-Seismic Applications" as defined in AISC 360.

* + 1. Weld Connections: Comply with AWS D1.1/D1.1M for tolerances, appearances, welding procedure specifications, weld quality, and methods used in correcting welding work.

Retain subparagraph below if built-up sections are required.

* + - 1. Assemble and weld built-up sections by methods that will maintain true alignment of axes without exceeding tolerances in AISC 303 for mill material.
  1. SHOP PRIMING

Retain this article if shop priming is required.

* + 1. Shop prime steel surfaces except the following:

Retain, revise, or delete five subparagraphs below to suit Project.

* + - 1. Surfaces embedded in concrete or mortar. Extend priming of partially embedded members to a depth of 2 inches (50 mm).
      2. Surfaces to be field welded.
    1. Surface Preparation: Clean surfaces to be painted. Remove loose rust and mill scale and spatter, slag, or flux deposits. Prepare surfaces according to the following specifications and standards:

Retain surface-preparation standards in nine subparagraphs below or revise to suit Project. Subparagraphs are listed from least to most comprehensive surface preparation and from lowest to highest cost. Coordinate minimum surface-preparation requirements with selection of primers, paint, and coating systems. See Evaluations.

Cleaning in first and second subparagraphs below removes loose rust, mill scale, and paint. Cleaning in first subparagraph is minimum surface preparation accepted by AISC for painted steel.

* + - 1. SSPC-SP 3, "Power Tool Cleaning."
    1. Priming: Immediately after surface preparation, apply primer according to manufacturer's written instructions and at rate recommended by SSPC to provide a minimum dry film thickness of 1.5 mils (0.038 mm). Use priming methods that result in full coverage of joints, corners, edges, and exposed surfaces.

Retain first subparagraph below if paragraph above does not suffice. Stripe painting adds cost but helps ensure that hard-to-reach areas, such as crevices, inside corners, and welds, are thoroughly coated and that sharp edges receive adequate coverage.

Delete "Surface Preparation" and "Priming" paragraphs above if retaining paragraph below. SSPC-PS Guide 7.00 includes either SSPC-SP 2 or SSPC-SP 3 surface preparation and a limited choice of nonlead primers. SSPC sets a minimum dry film thickness of 1.5 mils (0.038 mm). These one-coat shop-painting systems are not expected to protect weather-exposed steel beyond a few months. Revise paragraph below to AISC 303 default thickness of 1 mil (0.025 mm) if permitted.

* 1. SOURCE QUALITY CONTROL

Retain this article if fabricator's shop testing is required and revise to suit local practices and requirements of authorities having jurisdiction. Consider deleting if requiring AISC-certified fabricators and if authorities having jurisdiction approve fabrication work without special inspections. Coordinate with "Fabricator Qualifications" Paragraph in "Quality Assurance" Article.

* + 1. Testing Agency: Owner will engage an independent testing and inspecting agency to perform shop tests and inspections and prepare test reports.
       1. Provide testing agency with access to places where structural-steel work is being fabricated or produced to perform tests and inspections.
       2. Correct deficiencies in Work that test reports and inspections indicate does not comply with the Contract Documents.

RCSC prescribes inspection for snug-tightened joints and testing and inspection for each method of pretensioning joints.

* + 1. Bolted Connections: Shop-bolted connections will be tested and inspected according to RCSC's "Specification for Structural Joints Using ASTM A 325 or A 490 Bolts."
    2. Welded Connections: In addition to visual inspection, shop-welded connections will be tested and inspected according to AWS D1.1/D1.1M and the following inspection procedures, at testing agency's option:

Retain applicable nondestructive testing methods in four subparagraphs below. Revise to indicate extent of weld inspections if applicable and to insert alternative acceptance criteria to AWS D1.1/D1.1M if required.

* + - 1. Liquid Penetrant Inspection: ASTM E 165.
      2. Magnetic Particle Inspection: ASTM E 709; performed on root pass and on finished weld. Cracks or zones of incomplete fusion or penetration will not be accepted.
      3. Ultrasonic Inspection: ASTM E 164.
      4. Radiographic Inspection: ASTM E 94.

1. EXECUTION
   1. EXAMINATION
      1. Verify, with steel Erector present, elevations of concrete- and masonry-bearing surfaces and locations of anchor rods, bearing plates, and other embedments for compliance with requirements.
      2. Proceed with installation only after unsatisfactory conditions have been corrected.
   2. PREPARATION
      1. Provide temporary shores, guys, braces, and other supports during erection to keep structural steel secure, plumb, and in alignment against temporary construction loads and loads equal in intensity to design loads. Remove temporary supports when permanent structural steel, connections, and bracing are in place unless otherwise indicated.
   3. ERECTION
      1. Align and adjust various members that form part of complete frame or structure before permanently fastening. Before assembly, clean bearing surfaces and other surfaces that will be in permanent contact with members. Perform necessary adjustments to compensate for discrepancies in elevations and alignment.
         1. Level and plumb individual members of structure.
         2. Make allowances for difference between temperature at time of erection and mean temperature when structure is completed and in service.
      2. Splice members only where indicated.
      3. Do not use thermal cutting during erection.
      4. Do not enlarge unfair holes in members by burning or using drift pins. Ream holes that must be enlarged to admit bolts.
   4. FIELD CONNECTIONS
      1. High-Strength Bolts: Install high-strength bolts according to RCSC's "Specification for Structural Joints Using ASTM A 325 or A 490 Bolts" for type of bolt and type of joint specified.

RCSC requires that joint types be specified in the Contract Documents for most loading conditions. See Evaluations for a discussion of the joint types in subparagraph below, which are the three types RCSC now recognizes. Insert particular bolt pretensioning method for pretensioned or slip-critical joints if required; RCSC states that each type can provide satisfactory results.

* + - 1. Joint Type: Snug tightened.
    1. Weld Connections: Comply with AWS D1.1/D1.1M for tolerances, appearances, welding procedure specifications, weld quality, and methods used in correcting welding work.
       1. Comply with AISC 303 and AISC 360 for bearing, alignment, adequacy of temporary connections, and removal of paint on surfaces adjacent to field welds.
       2. Remove backing bars or runoff tabs, back gouge, and grind steel smooth.
       3. Assemble and weld built-up sections by methods that will maintain true alignment of axes without exceeding tolerances in AISC's "Code of Standard Practice for Steel Buildings and Bridges" for mill material.
  1. FIELD QUALITY CONTROL
     1. Testing Agency: Owner will engage a qualified independent testing and inspecting agency to inspect field welds and high-strength bolted connections.
     2. Bolted Connections: Bolted connections will be tested and inspected according to RCSC's "Specification for Structural Joints Using ASTM A 325 or A 490 Bolts."
     3. Welded Connections: Field welds will be visually inspected according to AWS D1.1/D1.1M.

Retain subparagraph below if required.

* + - 1. In addition to visual inspection, field welds will be tested and inspected according to AWS D1.1/D1.1M and the following inspection procedures, at testing agency's option:

Retain applicable nondestructive testing methods in four subparagraphs below. Revise to indicate extent of weld inspections if applicable and to insert alternative acceptance criteria to AWS D1.1/D1.1M if required.

* + - * 1. Liquid Penetrant Inspection: ASTM E 165.
        2. Magnetic Particle Inspection: ASTM E 709; performed on root pass and on finished weld. Cracks or zones of incomplete fusion or penetration will not be accepted.
        3. Ultrasonic Inspection: ASTM E 164.
        4. Radiographic Inspection: ASTM E 94.
    1. Correct deficiencies in Work that test reports and inspections indicate does not comply with the Contract Documents.

**END OF SECTION**