- GENERAL

  - SUMMARY

    - Furnish and install a UL listed system of electric self-regulating heating cable and components for maintaining the water temperature in the pipes as indicated on the drawings.

  - CODES AND STANDARDS

    - Codes and Standards shall be the current version adopted by the Authority Having Jurisdiction.

  - SUBMITTALS

    - Copy of UL file indicating the heating cable is specifically listed to provide freeze-protection.

    - Manufacturer's catalog cuts showing materials and performance data.

    - Project list of at least 20 projects, installed for at least 5 years, with at least 2000 ft (600m) of heating cable in each project.

- PRODUCTS

  - CONSTRUCTION

    - The self-regulating heating cable shall consist of two (2) 16-AWG nickel-coated copper bus wires embedded in a radiation-crosslinked conductive polymer core.  It shall be covered by a radiation-crosslinked, polyolefin, dielectric jacket and enclosed in a tinned copper braid of 14 AWG equivalent ware size.  The braid shall be covered with a (nominal) 40-mil polyolefin outer jacket, color coded for easy identification.  The cable shall be specifically designed, manufactured, and UL listed for freeze-protection.

  - MECHANICAL

    - The cable shall have a minimum cut-through resistance of 600 lb per CSA 22.2 0.3.  Cutting test 4.14.  The cable shall have a minimum impact resistance of 25 ft lb per UL 1588.11.  The cable shall withstand a glancing impact of 22 ft lb per UL 1581.590.  The cable shall have a minimum abrasion resistance of 7000 cycles per UL 719.19.  The cable shall withstand a crush resistance of 4500 N per IEEE 515 Deformation Test 5.1.5.

  - EXPERIENCE

    - The manufacturer shall have more than ten years experience with self-regulating heating cables for temperature maintenance of domestic hot water.

    - The manufacturer's Quality Assurance Program shall be certified to ISO 9001 standard.

  - ACCEPTABLE MANUFACTURER

    - Raychem Corporation.

    - Thermon.

    - Nelson Heat Tracing Systems.

    - Or Approved Equal.

- EXECUTION

  - OPERATING TEMPERATURES

    - The freeze protection system shall not exceed a nominal temperature of 40ºF.

  - MAINTENANCE TEMPERATURE

    - Each freeze protection system shall be maintained using only one product.  Temperatures shall be maintained with straight runs of heating cable on the pipe.  The use of a 40ºF fixed thermostat shall ensure heating cable is off when pipe temperature is over 40ºF.

  - INSTALLATION

    - The system shall be installed by factory trained certified installers.

    - The system shall be installed according to the drawings and the manufacturer's instruction.  The installer shall be responsible for providing a functional system, installed in accordance with applicable national and local code requirements.  Each circuit shall be protected with a 30-mA ground-fault protection device.

    - Electrical Connections:  The following requirements apply:

      - Electrical power wiring is specified in Division 26.

      - Freeze-protection for the fire line shall be monitored by fire alarm control panel.

    - Insulate heat traced piping in accordance with the manufacturer’s installation instructions and with Division 23.

  - TESTING

    - Procedure:  Measure the heater circuit continuity and the insulation resistance between the braid and bus wires with a 2500-Vdc megohmmeter (megger).

    - Acceptable Results:  The heater circuit shall be continuous and megger readings shall be at least 20 megohms regardless of heater length.  Circuits yielding unacceptable readings must be repaired or replaced.

    - Submittal of Results:  Submit records of the test data to the Construction Manager.

END OF SECTION