- GENERAL

  - RELATED DOCUMENTS

    - Drawings and Divisions 00 and 01, apply to this Section.

    - Related Sections:

      - Division 23.

  - SUMMARY

    - This Section includes condensate receiver/pumps for low-pressure steam systems.

  - SUBMITTALS

    - Product Data:  Include certified performance curves and rated capacities; shipping, installed, and operating weights; furnished specialties; and accessories for each type of product.  Indicate pump's operating point on curves.  Include receiver capacity and material.

    - Shop Drawings:  Show pump layout and connections.  Include Setting Drawings with templates for installing foundation and anchor bolts and other anchorages.

      - Wiring Diagrams:  Detail wiring for power, signal, and control systems and differentiate between manufacturer-installed and field-installed wiring.

    - Maintenance Data:  Include in maintenance manuals specified in Division 01.

  - CODES AND STANDARDS

    - Codes and Standards shall be the current version adopted by the Authority Having Jurisdiction.

  - QUALITY ASSURANCE

    - Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction.

    - ASME Compliance:  Fabricate and label receivers to comply with ASME Boiler and Pressure Vessel Code:  Section VIII, "Pressure Vessels," Division 01.

  - DELIVERY, STORAGE, AND HANDLING

    - Manufacturer's Preparation for Shipping:  Clean flanges and exposed machined metal surfaces and treat with anticorrosion compound after assembly and testing.  Protect flanges, pipe openings, and nozzles with wooden flange covers or with screwed-in plugs.

    - Store steam condensate pumps in dry location.

    - Retain protective covers for flanges and protective coatings during storage.

    - Protect bearings and couplings against damage from sand, grit, and other foreign matter.

  - COORDINATION

    - Coordinate size and location of concrete housekeeping pads.  Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork requirements are specified in Division 03.

- PRODUCTS

  - MANUFACTURERS

    - Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

      - Floor-Mounted, Condensate Receiver/Pumps:

        - ITT Fluid Handling; Div. of ITT Fluid Technology Corp.

        - Skidmore Div.; Vent-Rite Valve Corp.

        - Weil Pump Company, Inc.

        - Shipco.

        - Or Approved Equal

  - CONDENSATE RECEIVER/PUMPS

    - Description:  Factory-fabricated, packaged, electric-drive pump units; with receiver, pumps, controls, and accessories suitable for operation with low-pressure steam condensate.

    - Configuration:  Floor-mounting, simplex unit with receiver and float switch.

      - Receiver:  Floor-mounting, [close-grained cast iron][welded steel]; with externally adjustable float switch and flange for pump mounting.  Provide connection for atmospheric pressure vent.

      - Pump:  Centrifugal; close coupled; vertical design; permanently aligned; bronze fitted, and with enclosed bronze case ring and mechanical seal; and mounted on receiver flange.

      - Factory Wiring:  Between pump and float switch, for single external electrical connection.

    - Configuration:  Floor-mounting, duplex unit with receiver and unit mounted control panel.

      - Receiver:  Floor-mounting, [close-grained cast iron][welded steel]; with externally adjustable float switches and flanges for pump mounting.  Provide connection for atmospheric pressure vent.

      - Pumps:  Centrifugal; close coupled; vertical design; permanently aligned; bronze fitted, and with enclosed bronze case rings, mechanical seals suitable for 220 degrees F, and independent pump control circuit for each pump; and mounted on receiver flanges.

      - Float Switches:  Set for lead/lag operation.

      - Factory Wiring:  Between pumps, float switches, and control panel.

      - Control Panel:  NEMA 250, Type 2 enclosure with hinged door and grounding lug, mounted on unit; factory wired for single external electrical connection; and with the following included within cabinet:

        - Motor controller for each pump.

        - Electrical alternator.

        - Numbered terminal strip.

        - Disconnect switch.

        - Fused transformer for each control circuit.

      - Options:  Provide the following options:

        - Gauge glass level indicator.

        - Thermometer.

        - Discharge pressure gauges.

        - Discharge check valves.

        - High level alarm with dry contacts for monitoring by the DDC system.

- EXECUTION

  - EXAMINATION

    - Examine equipment foundations and anchor-bolt locations for compliance with requirements for installation.

    - Proceed with installation only after unsatisfactory conditions have been corrected.

  - CONDENSATE RECEIVER/PUMPS INSTALLATION

    - Install receiver/pumps according to manufacturer's written instructions.

    - Install pumps to provide access for periodic maintenance, including removing motors, impellers, couplings, and accessories.

    - Support pumps and piping separately, so piping is not supported by pumps.

    - Install receiver/pumps on 4-inch high concrete housekeeping pads.  Anchor to bases using inserts or anchor bolts.

    - Install thermometers and pressure gages.

  - CONNECTIONS

    - Piping installation requirements are specified in other Division 23 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

    - Install piping adjacent to machine to allow service and maintenance.

    - Install shutoff valves on inlet of units.

    - Install inlet strainer and valved bypass to drain at system return connection.

    - Install union, check valve, and shutoff valve at pump discharge connections for each pump.

    - Install pipe drain to nearest floor drain for overflow and drain piping connections.

    - Install full-size vent piping, terminating outside in 180-degree elbow at point above highest steam system connection or as indicated.

    - Install electrical connections for power, controls, and devices.

    - Electrical power and control wiring and connections are specified in Division 26 Sections.

    - Ground equipment.

      - Tighten electrical connectors and terminals according to manufacturer's published torque-tightening values.  If manufacturer's torque values are not indicated, use those specified in UL 486A and UL 486B.

  - START-UP PROCEDURES

    - Verify that condensate receiver/pumps are installed and connected according to the Contract Documents.

    - Verify that electrical wiring installation complies with manufacturer's written instructions and the Contract Documents.

    - Complete installation and startup checks according to manufacturer's written instructions.

    - Clean strainers.

    - Set condensate receiver/pumps controls.

    - Set pump controls for automatic start, stop, and alarm operation.

    - Perform the following preventive maintenance operations and checks before starting:

      - Lubricate bearings.

      - Set float switches to operate at proper levels.

      - Set throttling valves on pump discharge for specified flow.

      - Check motors for proper rotation.

      - Test pump controls and demonstrate compliance with requirements.

      - Replace damaged or malfunctioning pump controls and equipment.

      - Verify that pump controls are correct for required application.

    - Start condensate pumps according to manufacturer's written startup instructions.

  - DEMONSTRATION

    - Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain condensate receiver/pumps as specified below:

      - Train Owner's maintenance personnel on procedures and schedules for starting and stopping, troubleshooting, servicing, and maintaining pumps.

      - Review data in maintenance manuals.  Refer to Division 01 Operation and Maintenance Manual requirements.

      - Schedule training with Owner, through Architect, with at least seven days' advance notice.

END OF SECTION